## Readme
All Town Reconciliation Strategies - Northern Planning Region - Summary per Municipality, per Province
DWS Contract No. WP10587
The Department of Water and Sanitation (DWS) commissioned four three-year studies (2012/2013 - 2014/2015) for the continuation and maintenance of the bulk water supply reconciliation strategies for all towns in the country. The studies cover the four Water Resource Planning Areas - North, South, East and Central and this study covers the Northern Planning Area. These strategies were developed in 2011 and need to be revised to remain relevant under prevailing conditions. The study is part of an on-going process to ensure sufficient water can be made available for pertinent developmental imperatives in and around all towns.
A strategy was developed for each cluster - referring to a supply area/s (water supply scheme/s) utilising the same source.
Assumptions were made on the potential WC/WDM savings that can be achieved.
Assumptions were made on the augmentation options and implementation thereof to address future water requirements. Actual augmentation options may require futher studies - refer to individual strategy reports for confirmation.

## A1___PopWaterReq
All Town Reconciliation Strategies - Northern Planning Region - Summary for Limpopo Province
DWS Contract No. WP10587
ATRpt ID No. 2015 | Province | DM | LM | Cluster / Towns | Comment | Water Balance | Executive Summary | Conclusions & Recom-mendations | Estimated population, 2011 - 2035, High scenario | [5 empty] | Water Requirements (mil m³/a), High Scenario (WC/WDM not included) | [5 empty] | Unit Consumption (l/cap/day) |  |  | WC/WDM possible savings (mil m³/a) | [5 empty] | Water Balance, high scenario (mil m³/a, with WC/WDM, WITH augmentation) (<0 = red; >4 = blue) | [5 empty] | Water Source - Current
[9 empty] | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | 2011 | 2030 | 2035 | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | Name of Dam/River/Scheme | SurfaceW Licensed / Allocation (mil m³/a) | SW Supply (mil m³/a) | SW Quality | GroundW Licensed / Allocation (mil m³/a) | GW Supply (mil m³/a) | GW Quality
112 | LP | Waterberg | Thabazimbi | Leeupoort & Raphuti | Cluster currently in deficit (if WC/WDM not taken into account). Supply can be augmented via pipeline supplying Rooiberg nearby. High per capita consumption. | Graph 112 | Exec Sum | Recomm | 2448 | 2689 | 2916 | 3100 | 3250 |  | 0.147 | 0.174 | 0.211 | 0.239 | 0.256 |  | 164.4053 | 215.6584 | 215.6584 | 0.001 | 0.016 | 0.027 | 0.031 | 0.033 |  | 0.128 | 0.113 | 0.1 | 0.075 | 0.05 | 0.035 | BH | N/A | N/A | N/A |  | 0.048 | GW high in fluorides, but treated with RO
113 |  |  |  | Northam | Water supplied and water requirements to be verified. | Graph 113 | Exec Sum | Recomm | 8745 | 9678 | 10568 | 11298 | 11890 |  | 0.868 | 1.009 | 1.229 | 1.382 | 1.454 |  | 271.7501 | 334.8053 | 334.8053 | 0.009 | 0.091 | 0.16 | 0.18 | 0.189 |  | 3.43 | 3.361 | 4.762 | 4.611 | 4.478 | 4.415 | Vaalkop Dam |  | 0.73 | Good | N/A | N/A | N/A
|  |  |  | Northam | Tables from Executive Summary | Graph 113 |  |  | 8745 | 9678 | 10568 | 11298 | 11890 |  | 0.392 | 0.455 | 0.555 | 0.624 | 0.656 |  | 122.7258 | 151.0538 | 151.0538 | 0.004 | 0.041 | 0.072 | 0.081 | 0.085 |  | 0.373 | 0.707 | 0.671 | 0.612 | 0.552 | 0.524
114 |  |  |  | Rooiberg | The delivery capacity of the newly built bulk supply pipe line from Zandrivierspoort to Rooiberg is less than planned (150mm diameter was installed instead of 250mm), therefore the full allocation of water cannot be utilized. Even so Rooiberg would still have sufficient volumes. | Graph 114 | Exec Sum | Recomm | 1677 | 1858 | 2029 | 2169 | 2282 |  | 0.075 | 0.088 | 0.107 | 0.12 | 0.126 |  | 122.4441 |  | 151.1697 | 0.001 | 0.008 | 0.014 | 0.016 | 0.016 |  | 0.685 | 0.679 | 0.673 | 0.66 | 0.649 | 0.643 | BH | N/A | N/A | N/A |  | 0.753 | GW high in fluorides
25 |  |  |  | Thabazimbi Urban | GW supplied to domestic & mining consumers, exact split in quantities not known | Graph 25 | Exec Sum | Recomm | 19392 | 21462 | 23431 | 25046 | 26361 |  | 0.868 | 1.009 | 1.229 | 1.382 | 1.454 |  | 122.5482 |  | 151.0123 | 0.009 | 0.091 | 0.16 | 0.18 | 0.189 |  | 3.43 | 3.361 | 4.762 | 4.611 | 4.478 | 4.415 | Vaalkop Dam |  | 3.285 | Good |  | 1.665 | Chlorinated prior to distribution
115 |  |  | Lephalale | Ga-Seleka | Rural commercial farming area, BH use between domestic & irrigation not exactly clear | Graph 115 | Exec Sum | Recomm | 20770 | 21439 | 23169 | 24754 | 25845 |  | 1.145 | 1.29 | 1.513 | 1.65 | 1.698 |  | 150.9311 |  | 179.875 | 0.011 | 0.116 | 0.197 | 0.214 | 0.221 |  | 0.658 | 0.607 | 0.566 | 0.424 | 0.305 | 0.262 | BH | N/A | N/A | N/A | 1.09 | 1.13 | Acceptable, but some areas high N, F, TDS. No WTW.
116 |  |  |  | Lephalale (Ellisras Urban)* | Strategic area due to the potential high increase in water requirements (due to domestic developments, power generation, mining). Mines also provide water to domestic consumers (Marapong township). | Graph 116 | Exec Sum | Recomm | 32051 | 58655 | 114144 | 122463 | 129724 | 133457 | 27.962 | 36.163 | 62.26 | 88.39 | 113.28 | 116.74 | 2388.5615 | 2390.7969 | 2394.904 | 0 | 0 | 1.05 | 1.05 | 1.05 | 1.05 | 16.788 | 8.587 | 67.78 | 41.65 | 16.76 | 13.3 | Mokolo Dam | 9.9 Grootgeluk Coal Mine 7.3 Matimba Power Station 1.0 Lephalale 10.4 Irrigation Scheme | 44.6 | - | - | 0.15 | High fluorides
|  |  |  | Lephalale (Ellisras Urban)* | * Super High Scenario - due to potential urban, mining and industrial (power generation) development in the region. | Graph 116 | Exec Sum | Recomm | 16534 | 17870 | 19091 | 19930 | 20520 |  | 2.226 | 8.472 | 17.307 | 17.674 | 18.361 |  | 368.6014 | 2449.7894 | 2449.7894 | 0.022 | 0.762 | 2.25 | 2.298 | 2.387 |  | 4.146 | 2.947 | -2.56 | -9.907 | -10.226 | -10.824 | Mokolo Dam, augmentation via transfer scheme from the Crocodile West catchment
117 |  |  |  | Lephalale Shongwane | Cluster currently in deficit. | Graph 117 | Exec Sum | Recomm | 13605 | 12408 | 11494 | 11035 | 10530 |  | 0.69 | 0.657 | 0.671 | 0.674 | 0.643 |  | 138.8546 | 167.1831 | 167.1831 | 0.007 | 0.059 | 0.087 | 0.088 | 0.084 |  | -0.38 | -0.333 | -0.248 | -0.234 | -0.237 | -0.21 | BH | N/A | N/A | N/A |  | 0.35 | Acceptable, but high nitrate & fluoride - requires treatment. No WTW.
118 |  |  |  | Mokuranyane |  | Graph 118 | Exec Sum | Recomm | 17220 | 18612 | 19888 | 20760 | 21378 |  | 0.88 | 0.994 | 1.17 | 1.278 | 1.316 |  | 139.9134 | 168.5383 | 168.5383 | 0.009 | 0.089 | 0.152 | 0.166 | 0.171 |  | 0.508 | 0.468 | 0.436 | 0.322 | 0.228 | 0.195 | BH | N/A | N/A | N/A |  | 1.34 | Acceptable, but some areas high N, F, TDS. No WTW.
119 |  |  |  | Witpoort |  | Graph 119 | Exec Sum | Recomm | 12946 | 13991 | 14951 | 15609 | 16069 |  | 0.657 | 0.742 | 0.874 | 0.955 | 0.983 |  | 138.9439 | 167.4844 | 167.4844 | 0.007 | 0.067 | 0.114 | 0.124 | 0.128 |  | 0.485 | 0.455 | 0.431 | 0.345 | 0.275 | 0.251 | BH | N/A | N/A | N/A | 0.003 | 1.106 | Acceptable, but some areas high N, F, TDS. No WTW.
231 |  |  | Mookgopong | Mookgophong LM Farms | No strategy available
120 |  |  |  | Mookgophong RWS (Naboomspuit) | Cluster currently in deficit. Over-abstraction of GW resources. | Graph 120 | Exec Sum | Recomm | 32741 | 35216 | 37443 | 39289 | 40658 |  | 1.673 | 1.879 | 2.202 | 2.417 | 2.501 |  | 139.8987 | 168.4137 | 168.4137 | 0 | 0 | 0 | 0 | 0 |  | -0.534 | 0.055 | 0.195 | 0.322 | 0.107 | 0.023 | Frikkie Geyser Dam, Nyl wellfield | 0.42 | 0.504 |  |  | 0.936 | Good
121 |  |  | Modimolle | Mabaleng (Alma) | Cluster currently in deficit. | Graph 121 | Exec Sum | Recomm | 1907 | 1859 | 1793 | 1743 | 1683 |  | 0.095 | 0.101 | 0.119 | 0.127 | 0.122 |  | 136.39 | 198.4657 | 198.4657 | 0 | 0 | 0 | 0 |  |  | -0.007 | 0.011 | 0.033 | 0.031 | 0.025 | 0.029 | BH | N/A | N/A | N/A |  | 0.085 | Variable (good to elevated fluoride levels). No WTW
122 |  |  |  | Mabatlane (Vaalwater) | Cluster currently in deficit. | Graph 122 | Exec Sum | Recomm | 18398 | 20724 | 23017 | 24939 | 26507 |  | 0.876 | 1.034 | 1.274 | 1.448 | 1.539 |  | 130.3597 | 158.96 | 158.96 | 0 | 0 | 0 | 0 | 0 |  | -0.107 | 0.154 | 0.226 | 0.158 | 0.132 | 0.041 | BH | N/A | N/A | N/A | 0.036 | 0.68 | Good
123 |  |  |  | Modimolle Urban (Nylstroom) |  | Graph 123 | Exec Sum | Recomm | 43995 | 49557 | 55040 | 59636 | 63385 |  | 2.097 | 2.474 | 3.048 | 3.464 | 3.682 |  | 130.4983 | 159.0403 | 159.0403 | 0 | 0 | 0 |  | 0 |  | 1.14 | 0.926 | 0.549 | 0.425 | 0.219 | 0.001 | Donkerpoort Dam, Roodeplaat Dam, BH | 1.99 | 2.923 |  | 0.1 | 0.1 | Good
124 |  |  | Bela-Bela | Bela-Bela Urban | Cluster currently in deficit. Water requirements include domestic & commercial users. | Graph 124 | Exec Sum | Recomm | 29663 | 32234 | 34472 | 35590 | 36252 |  | 2.802 | 3.053 | 3.401 | 3.584 | 3.637 |  | 258.6204 | 274.6762 | 274.6762 | 0 | 0 | 0 | 0 | 0 |  | -0.331 | 0.269 | 0.318 | 0.17 | 0.087 | 0.034 | Platrivier Dam, Roodeplaat Dam, BH | 1.209 | 1.861 | Potable water 96% SANS compliant | 0.38 | 0.51 | Variable, water treated at WTW.
125 |  |  |  | Pienaarsrivier |  | Graph 125 | Exec Sum | Recomm | 1980 | 1976 | 1962 | 2002 | 2028 |  | 0.133 | 0.137 | 0.147 | 0.155 | 0.157 |  | 183.9061 | 211.9539 | 211.9539 | 0.001 | 0.012 | 0.019 | 0.02 | 0.02 |  | 0.115 | 0.114 | 0.098 | 0.082 | 0.072 | 0.07 | Roodeplaat Dam | 0.248 | 0.248 | Good | N/A | N/A | N/A
126 |  |  |  | Rapotkwane |  | Graph 126 | Exec Sum | Recomm | 2097 | 2094 | 2079 | 2119 | 2149 |  | 0.032 | 0.036 | 0.047 | 0.054 | 0.055 |  | 41.7793 | 70.0706 | 70.0706 | 0 | 0 | 0 | 0 | 0 |  | 0.202 | 0.201 | 0.197 | 0.186 | 0.179 | 0.178 | BH | N/A | N/A | N/A |  | 0.233 | Good
127 |  |  | Mogalakwena | Bakenberg | Cluster currently in deficit. Poor GW quality. No WTW | Graph 127 | Exec Sum | Recomm | 61702 | 61035 | 61427 | 61986 | 62145 |  | 2.519 | 2.63 | 2.981 | 3.177 | 3.185 |  | 111.7735 | 140.3179 | 140.3179 | 0.025 | 0.237 | 0.388 | 0.413 | 0.414 |  | -1.634 | -1.634 | -1.533 | -1.733 | -1.904 | -1.911 | BH | N/A | N/A | N/A | 0.86 | 0.86 | Poor. No WTW.
128 |  |  |  | Ga-Phahladira | Cluster currently in deficit. | Graph 128 | Exec Sum | Recomm | 1653 | 1644 | 1666 | 1687 | 1695 |  | 0.025 | 0.028 | 0.038 | 0.043 | 0.043 |  | 41.4073 | 69.4558 | 69.4558 | 0 | 0.003 | 0.005 | 0.006 | 0.006 |  | 0 | -0.001 | -0.002 | -0.009 | -0.013 | -0.014 | BH | N/A | N/A | N/A |  | 0.024
129 |  |  |  | Mapela | Cluster currently in deficit. Poor infrastructure (ageing, O&M lacking) | Graph 129 | Exec Sum | Recomm | 100957 | 105648 | 109741 | 113396 | 115823 |  | 4.473 | 4.92 | 5.708 | 6.206 | 6.339 |  | 121.3032 | 149.8427 | 149.8427 | 0.045 | 0.43 | 0.742 | 0.807 | 0.824 |  | -2.758 | -2.938 | -2.988 | -3.476 | -3.909 | -4.025 | BH | N/A | N/A | N/A |  | 1.49 | Elevated levels of nitrates, fluorides, salts. No WTW. Poor condition of infrastructure.
130 |  |  |  | Mokopane |  | Graph 130 | Exec Sum | Recomm | 92892 | 97049 | 100711 | 103994 | 106157 |  | 3.825 | 4.216 | 4.922 | 5.366 | 5.477 |  | 112.7361 | 141.255 | 141.255 | 0.038 | 0.379 | 0.64 | 0.698 | 0.712 |  | 3.319 | 3.167 | 3.117 | 2.671 | 2.285 | 2.188 | Doorndraai Dam, BH | 4.38 | 4.38 | Good |  | 2.573 | No information, threats including mining & on-site sanitation
131 |  |  |  | Rebone & Glen Alpine | Glen Alpine Dam possible future source for augmentation. O&M causing intermittent water supplies. | Graph 131 | Exec Sum | Recomm | 71119 | 78882 | 84799 | 89839 | 93650 |  | 3.173 | 3.699 | 4.437 | 4.945 | 5.155 |  | 122.1502 | 150.706 | 150.706 | 0.032 | 0.333 | 0.577 | 0.643 | 0.67 |  | 0.774 | 0.509 | 0.285 | -0.209 | -0.651 | -0.834 | BH | N/A | N/A | N/A |  | 0.765 | Marginal - elevated levels of nitrates, fluorides, hardness, salts

## 113
Executive Summary

## 116
Lephalae Cluster water balance
Lephalae Cluster water balance
Augmentation options and/or implementation of WC/WDM measures
Augmentation options and/or implementation of WC/WDM measures