## Readme
All Town Reconciliation Strategies - Northern Planning Region - Summary per Municipality, per Province
DWS Contract No. WP10587
The Department of Water and Sanitation (DWS) commissioned four three-year studies (2012/2013 - 2014/2015) for the continuation and maintenance of the bulk water supply reconciliation strategies for all towns in the country. The studies cover the four Water Resource Planning Areas - North, South, East and Central and this study covers the Northern Planning Area. These strategies were developed in 2011 and need to be revised to remain relevant under prevailing conditions. The study is part of an on-going process to ensure sufficient water can be made available for pertinent developmental imperatives in and around all towns.
A strategy was developed for each cluster - referring to a supply area/s (water supply scheme/s) utilising the same source.
Assumptions were made on the potential WC/WDM savings that can be achieved.
Assumptions were made on the augmentation options and implementation thereof to address future water requirements. Actual augmentation options may require futher studies - refer to individual strategy reports for confirmation.

## A1___PopWaterReq
All Town Reconciliation Strategies - Northern Planning Region - Summary for North West Province
DWS Contract No. WP10587
ATRpt ID No. 2015 | Province | DM | LM | Cluster / Towns | Comment | Water Balance | Executive Summary | Conclusions & Recom-mendations | Estimated population, 2008 - 2030, High scenario | [7 empty] | Water Requirements (mil m³/a), High Scenario (WC/WDM not included) | [7 empty] | Unit Consumption (l/cap/day) |  |  |  | WC/WDM possible savings (mil m³/a) | [7 empty] | Water Balance, high scenario (mil m³/a, with WC/WDM, WITH augmentation) | [7 empty] | Water Source - Current
[9 empty] | 2008 | 2010 | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | 2008 | 2010 | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | 2008 | 2011 | 2030 | 2035 | 2008 | 2010 | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | 2008 | 2010 | 2011 | 2015 | 2020 | 2025 | 2030 | 2035 | Name of Dam/River/Scheme | SurfaceW Licensed / Allocation (mil m³/a) | SW Supply (mil m³/a) | SW Quality | GroundW Licensed / Allocation (mil m³/a) | GW Supply (mil m³/a) | GW Quality | Level of Confidence in Info
202 |  | Ngaka Modiri Molema | Mafikeng | Mafikeng |  | graph 202 | ExecSummary | Recommendation |  |  | 213960 | 224416 | 226975 | 229293 | 234298 | 239412 |  |  | 12.378 | 13.461 | 14.064 | 14.658 | 15.068 | 15.457 |  | 158.39 |  | 176.7621 |  |  | 0 | 0.269 | 0.703 | 0.738 | 0.753 | 0.773 |  |  | -5.658 | -6.18 | -5.73 | -5.981 | -6.235 | -6.505 | Setumo Dam, GW | 5.3 | 4.38 | deteriorating due to bacteriological contamination and eutrification | 10.95 | 10.576 | Acceptable for drinking, Elevated magnesium and nitrate levels
201 |  |  |  | Madibe-Western |  | graph 201 | ExecSummary | Recommendation | 26407 | 26206 |  | 25808 | 26442 | 27017 | 27521 |  | 1.249 | 1.205 |  | 1.224 | 1.257 | 1.271 | 1.281 |  | 129.495 |  | 127.4368 |  | 1.249 | 1.22 |  | 1.267 | 1.328 | 1.371 | 1.41 |  | -0.596 | 0.083 |  | 0.066 | 0.055 | 0.062 | 0.023 |  | GW | 0 | 0 | N/A | 0 | 0.653 | Generally acceptable, although 50% is poor around in the Mabibe area | low
200 |  |  |  | Driehoek South/Maipeing |  | graph 200 | ExecSummary | Recommendation | 55186 | 52315 |  | 52444 | 52547 | 52622 | 53205 |  | 2.763 | 2.619 |  | 2.656 | 2.722 | 2.756 | 2.767 |  | 137.0761 |  | 142.3857 |  | 0 | 0 |  | 0 | 0 | 0 | 0 |  | -1.463 | 0.181 |  | 0.144 | 0.078 | 0.044 | 0.013 |  | GW | 0 |  | N/A | 1.9 | 0.653 | Varies from acceptable for drinking to poor quality, due to high concentrations of nitrates | low
203 |  |  |  | MigaNorth |  | graph 203 | ExecSummary | Recommendation | 16247 | 16666 |  | 17146 | 17573 | 17932 | 18462 |  | 0.773 | 0.793 |  | 0.829 | 0.876 | 0.908 | 0.934 |  | 130.2615 |  | 138.509 |  | 0 | 0.008 |  | 0.075 | 0.114 | 0.118 | 0.121 |  | -0.073 | 0.065 |  | 0.146 | 0.188 | 0.16 | 0.137 |  | GW | 0.006 | 0 | No Info | 0 | 0.7 | majority of water is acceptable,according to data from water services | low
204 |  |  |  | Wondermere |  | graph 204 | ExecSummary | Recommendation | 4586 | 4703 |  | 4836 | 4952 | 5049 | 5195 |  | 0.213 | 0.218 |  | 0.228 | 0.241 | 0.249 | 0.256 |  | 127.1614 |  | 134.9162 |  | 0 | 0.002 |  | 0.021 | 0.031 | 0.032 | 0.033 |  | 2.387 | 2.384 |  | 2.393 | 2.391 | 2.383 | 2.377 |  | GW | 0 | 0 | No Info | 0 | 2.6 | acceptable for drinking | low
34 |  |  | Ramotshere Moiloa | Khunotswane |  | graph 34 | ExecSummary | Recommendation | 4357 | 4442 |  | 4658 | 4824 | 4887 | 4925 |  | 0.213 | 0.219 |  | 0.24 | 0.275 | 0.292 | 0.294 |  | 133.8449 |  | 163.4372 |  | 0 | 0.002 |  | 0.022 | 0.036 | 0.038 | 0.038 |  | -0.209 | 0.007 |  | 0.016 | 0.015 | 0.01 | 0.008 |  | GW, Molatedi – Gaborone, Ngotwane and Motswedi - Gopane WSS | 0 | 0 | N/A | 0.004 | 0.004 | good | low
35 |  |  |  | Madutle |  | graph 35 | ExecSummary | Recommendation | 1088 | 1069 |  | 1060 | 1055 | 1060 | 1074 |  | 0 | 0.001 |  | 0.005 | 0.008 | 0.008 | 0.008 |  | 0 |  | 20.3937 |  | 0 | 0.001 |  | 0.005 | 0.008 | 0.008 | 0.008 |  | 0.051 | 0 |  | 0.002 | 0.005 | 0.002 | 0.001 |  | GW, Molatedi – Gaborone, Ngotwane and Motswedi - Gopane WSS | 0 | 0 | N/A | 0 | 0 | good | low
36 |  |  |  | Motswedi-Gopane |  | graph 36 | ExecSummary | Recommendation |  |  | 20273 | 20031 | 19969 | 19969 | 19980 | 19991 |  |  | 0.705 | 0.733 | 0.779 | 0.827 | 0.832 | 0.836 |  | 95.2096 |  | 114.4937 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | -0.043 | -0.071 | 0.057 | 0.009 | 0.004 | 0 | Sehujwande dam, GW | 0.839 | 0.839 | High turbidity |  | 0.042 | Varies from Class 0 -Class 2
37 |  |  |  | Reboile |  | graph 37 | ExecSummary | Recommendation | 2308 | 2220 |  | 2520 | 2076 | 2076 | 2105 |  | 0.109 | 0.111 |  | 0.118 | 0.124 | 0.126 |  |  | 129.3006 |  | 0 |  | 0 | 0.001 |  | 0.01 | 0.015 | 0.016 | 0.016 |  | 0.013 | 0.018 |  | 0.025 | 0.023 | 0.018 | 0.017 |  | GW | 0 | 0 | N/A | 1.702 | 0.126 | 78% - Ideal/Good 22% - health risk | low
38 |  |  |  | Zeerust |  | graph 38 | ExecSummary | Recommendation | 19037 | 19557 |  | 20785 | 21725 | 21831 | 22126 |  | 1.128 | 1.169 |  | 1.294 | 1.484 | 1.557 | 1.578 |  | 162.226 |  | 195.2603 |  | 1.128 | 1.169 |  | 1.294 | 1.484 | 1.557 | 1.578 |  | 0.252 | 0.223 |  | 0.202 | 0.089 | 0.026 | 0.008 |  | GW | 0 | 0 | No Info | 0 | 1.38 | Good | low
211 |  |  |  | Brakaagte, Leeufontein |  | graph 211 | ExecSummary | Recommendation | 15987 | 15648 |  | 15559 | 15424 | 15438 | 15656 |  | 0.721 | 0.712 |  | 0.744 | 0.821 | 0.864 | 0.876 |  | 123.4747 |  | 153.1909 |  | 0 | 0.007 |  | 0.067 | 0.107 | 0.112 | 0.114 |  | 0.179 | 0.615 |  | 0.673 | 0.676 | 0.638 | 0.628 |  | GW | 0 | 0 | N/A | 0.361 | 0.6 | poor, could be localised faecal and nitrate contimination of water due to porosity of the overlaying soils | low
212 |  |  |  | Dinokana |  | graph 212 | ExecSummary | Recommendation |  |  | 43399 | 44538 | 46029 | 46243 | 46932 | 47632 |  |  | 1.873 | 2.031 | 2.228 | 2.367 | 2.408 | 2.45 |  | 118.1593 |  | 140.8241 | [10 empty] | -0.194 | -0.352 | 0.051 | 0.083 | 0.042 | 0 | GW | 0 | 0 | N/A | 0 | 1.679 | good
213 |  |  |  | Kopfontein, Molatedi/Gabarone |  | graph 213 | ExecSummary | Recommendation | 450 | 438 |  | 425 | 413 | 413 | 421 |  | 0.022 | 0.022 |  | 0.022 | 0.024 | 0.025 | 0.025 |  | 133.8505 |  | 162.5802 |  | 0 | 0 |  | 0.002 | 0.003 | 0.003 | 0.003 |  | 0.005 | 0.005 |  | 0.007 | 0.006 | 0.005 | 0.005 |  | Molatedi Dam | 0 | 0.027 | Accepatable, no problems reported | 0 | 0 | no data available, however ogther data for ZQMDDP22426AC0001 for 2007 indicates poor quality (class 4) | low
214 |  |  |  | Mosweu |  | graph 214 | ExecSummary | Recommendation | 5550 | 5710 |  | 6073 | 6347 | 6380 | 6468 |  | 0.268 | 0.279 |  | 0.31 | 0.359 | 0.378 | 0.363 |  | 132.2061 |  | 153.6549 |  | 0 | 0.003 |  | 0.028 | 0.047 | 0.049 | 0.05 |  | 0.132 | 0.124 |  | 0.118 | 0.088 | 0.071 | 0.067 |  | GW | 0 | 0 | N/A | No Info | 0.4 | Good, elevated concentrations ofchloride, magnesium and nitrate | low
215 |  |  |  | Ngotwane |  | graph 215 | ExecSummary | Recommendation | 11286 | 11412 |  | 11863 | 12191 | 12234 | 12407 |  | 0.55 | 0.561 |  | 0.61 | 0.693 | 0.729 | 0.739 |  | 133.4235 |  | 163.075 |  | 0 | 0.006 |  | 0.055 | 0.09 | 0.095 | 0.096 |  | 0.25 | 0.495 |  | 0.495 | 0.447 | 0.436 | 0.427 |  | Ngotwane Dam, GW | 0 | 0 | No Info | 0 | 0.8 | data limited, 96% - ideal/accepatable 4% - poor | low
216 |  |  |  | Supingstadt |  | graph 216 | ExecSummary | Recommendation |  |  | 3821 | 3821 | 3973 | 4051 | 4093 | 4135 |  |  | 0.188 | 0.206 | 0.238 | 0.266 | 0.269 | 0.272 |  | 134.7071 |  | 180.0956 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | -0.048 | -0.066 | 0.034 | 0.006 | 0.003 | 0 | GW | 0 | 0 | No Info |  | 1.528 | Acceptable, suitable for long term use
217 |  |  |  | Witleigat/Lehurutse |  | graph 217 | ExecSummary | Recommendation | 19073 | 18239 |  | 17576 | 16948 | 16923 | 17154 |  | 0.861 | 0.832 |  | 0.841 | 0.903 | 0.948 | 0.961 |  | 123.593 |  | 153.3797 |  | 0 | 0.008 |  | 0.076 | 0.117 | 0.123 | 0.125 |  | -0.261 | 0.027 |  | 0.134 | 0.164 | 0.145 | 0.134 |  | GW, Molatedi – Gaborone, Ngotwane and Motswedi - Gopane WSS | 0 | 0 | N/A | 0 | 0.6 | good | low
192 |  |  |  | Koffiekraal,Mankwe-Madikwe |  | graph 192 | ExecSummary | Recommendation | 13219 | 13197 |  | 13430 | 13673 | 13783 | 13785 |  | 0.517 | 0.522 |  | 0.562 | 0.646 | 0.689 | 0.689 |  | 107.0784 |  | 136.8429 |  | 0 | 0.005 |  | 0.051 | 0.084 | 0.09 | 0.09 |  | 0.426 | 0.846 |  | 0.882 | 0.871 | 0.834 | 0.834 |  | GW | 0 | 0 | N/A | 0.963 | 0.943 | marginal, poorer groundwater quality could be associated with elevated magnesium and nitrates levels | low
209 |  |  | Ditsobotla | Matikiring |  | graph 209 | ExecSummary | Recommendation | 1914 | 1969 |  | 2024 | 2037 | 2035 | 2084 |  | 0.095 | 0.098 |  | 0.104 | 0.116 | 0.121 | 0.124 |  | 135.8912 |  | 162.9047 |  | 0 | 0 |  | 0.001 | 0.0012 | 0.0012 | 0.0012 |  | 1.795 | 1.792 |  | 1.787 | 1.775 | 1.77 | 1.767 |  | GW | 0 | 0 | N/A | 1.89 | 1.89 | acceptable for drinking | low
210 |  |  |  | Shiela |  | graph 210 | ExecSummary | Recommendation | 57783 | 60074 |  | 61208 | 61821 | 62247 | 63863 |  | 2.871 | 2.974 |  | 3.169 | 3.537 | 3.731 | 3.827 |  | 136.0326 |  | 164.0661 |  | 0 | 0 |  | 0.032 | 0.035 | 0.037 | 0.038 |  | 2.329 | 2.226 |  | 2.063 | 1.698 | 1.507 | 1.411 |  | Polfonteinspruit River, GW | 0 | 2.4 | No Info | 2.8 | 2.84 | acceptable for drinking | low