## Dummy
| PROJECT: | Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
| OPTION: | Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
| DATE: | April 2008
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
| DESCRIPTION |  | UNIT/RATE | P1 | P2 | P3 | P4 | P5 | P6 | TOTAL
| Start Chainage |  |  | 0 | 0 | 0
| End Chainage |  |  | 36380 | 0 | 0
PUMP HEAD AND FLOW RATE
| Flow rate (duty) (Qd) 347 day average flow |  | m³/s | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
| installed capacity (Qi = Qp x (1 + Ps)) |  | m³/s | 0.625 | 0.71301 | 0.71301 | 0 | 0 | 0
| Required peak capacity (Qp = Q365 x Peak Refill factor) |  | m³/s | 0.5 | 0.57041 | 0.57041 | 0 | 0 | 0
| Peak factor | 1.2
Head pumped (under normal operating conditions):
| static head (Hst) |  | m | 110 | 0 | 0 | 0 | 0 | 0 | 110
| rising main friction loss(Hf) |  | m | 68.8623 | 0 | 0 | 0 | 0 | 0 | 68.8623
| rising main secondary losses(Hv) |  | m | 9.095 | 0 | 0 | 0 | 0 | 0 | 9.095
| pump station secondary losses(Hps) |  | m | 4 | 0 | 0 | 0 | 0 | 0 | 4
| Total head (duty) (Hd = Hst + Hf + Hv + Hps) |  | m | 191.9573 | 0 | 0 | 0 | 0 | 0 | 191.9573
Head pumped (under peak operating conditions):
| static head (Hst) |  | m | 110 | 0 | 0 | 0 | 0 | 0 | 110
| rising main friction loss(Hf) |  | m | 68.8623 | 0 | 0 | 0 | 0 | 0 | 68.8623
| rising main secondary losses(Hv) |  | m | 9.095 | 0 | 0 | 0 | 0 | 0 | 9.095
| pump station secondary losses(Hps) |  | m | 4 | 0 | 0 | 0 | 0 | 0 | 4
| Total head (peak) (Hd = Hst + Hf + Hv + Hps) |  | m | 191.9573 | 0 | 0 | 0 | 0 | 0 | 191.9573
All further information on this sheet is calculated for normal operating conditions
RISING MAIN
| length (L) |  | m | 36380 | 0 | 0 | 0 | 0 | 0 | 36380
| outside diameter (OD) |  | mm | 700 | 700 | 700 | 0 | 0 | 0
| inner diameter (ID) |  | mm | 690 | 672 | 672 | 0 | 0 | 0
| minimum yield stress of steel |  | MPa | 290 | 290 | 290 | 0 | 0 | 0
| minimum wall thickness (tmin = D/160) |  | mm | 4 | 4 | 4 | 0 | 0 | 0
| required wall thickness (t) |  | mm | 5 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
| chosen wall thickness (t) |  | mm | 5 | 14 | 14 | 0 | 0 | 0
| number of pipes in parallel (n) |  | no | 1 | 1 | 1 | 1 | 1 | 1
| flow per pipe (Qp) |  | m³/s | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
| velocity per pipe (Vp) |  | m/s | 1.3372 | 1.4097 | 1.4097 | 0 | 0 | 0
| secondary losses in rising main |  | m/km | 0.25 | 0.25 | 0.25 | 0 | 0 | 0
INPUT FOR COLEBROOK-WHITE & DARCY-WEISBACH
| friction coefficient (l) |  | - | 0.014332 | 0.01435 | 0.01435 | #DIV/0! | #DIV/0! | #DIV/0!
| effective roughness (k) |  | mm | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Reynolds number (Re) |  | - | 816493.2312 | 838363.5856 | 838363.5856 | 0 | 0 | 0
| pipe cross sectional area (A) |  | m² | 0.37393 | 0.35467 | 0.35467 | 0 | 0 | 0
| kinematic viscosity (nu) |  | m²/s | 1.13e-06 | 1.13e-06 | 1.13e-06 | 1.13e-06 | 1.13e-06 | 1.13e-06
| gravity constant (g) |  | m/s² | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81
PUMP SET EFFICIENCIES
| Efficiency of pump (Ep) |  | % | 90% | 90% | 90% | 90% | 90% | 90%
| Efficiency of motor (Em) |  | % | 97% | 97% | 97% | 97% | 97% | 97%
| Average loss in efficiency between major overhauls (Eo) |  | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
| Overall efficiency (Et = Ep x Em x (1 - Eo)) |  | % | 85.99% | 85.99% | 85.99% | 85.99% | 85.99% | 85.99%
| MW/MVA ratio (power factor Pf) |  | - | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
| Standby allowance (Ps) |  | % | 25% | 25% | 25% | 25% | 25% | 25%
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
| DESCRIPTION |  | UNIT/RATE | P1 | P2 | P3 | P4 | P5 | P6 | TOTAL
PUMP STATION POWER REQUIREMENTS
| power req'd at duty point (Pd = 9.81 x 1000 x Qd x Hd / Et) |  | MW | 1.0949 | 0 | 0 | 0 | 0 | 0 | 1.0949
| power absorbed at Qd: (Pd / Pf) |  | MVA | 1.1406 | 0 | 0 | 0 | 0 | 0 | 1.1406
| power absorbed at Qi: (Pd x Pf x (1 + Ps)) |  | MVA | 1.4257 | 0 | 0 | 0 | 0 | 0 | 1.4257
| head pumped (Hd) |  | m | 191.9573 | 0 | 0 | 0 | 0 | 0 | 191.9573
| Energy consumed over 24 hours (continuous use) | 24 | MWh | 26.2787 | 0 | 0 | 0 | 0 | 0 | 26.2787
Paramater used for pump stations costing | power req'd at peak point (Pp = 9.81 x 1000 x Qp x Hp / Et) |  | MW | 1.0949 | 0 | 0 | 0 | 0 | 0 | 1.0949
ADDITIONAL PUMP STATION PARAMETERS
| Access road to pump station |  | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BREAKDOWN OF COSTS FOR USE IN TABLE 2:
0 Included in Weir Cost | Hours of storage in forebay (Ts) |  | h | 0 | 0 | 0 | 0 | 0 | 0
| Forebay volume (Vf = Qd x Ts) |  | m³ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COST OF ELEC/ | COST OF PUMP/ | COST OF CIVIL | TRANSMISSION | TOTAL
| PUMP STATION COST (single stage vertical) | [9 empty] | MECH EQUIPMENT | MOTOR ONLY | CONSTRUCTION | LINE COST | (CHECK)
| mechanical: pump & motor | 60% | of total A1 | 5193498.7591 | 0 | 0 | 0 | 0 | 0 | 5193498.7591 |  | 5193498.7591
| mechanical: valves | 25% | of total A1 | 2163957.8163 | 0 | 0 | 0 | 0 | 0 | 2163957.8163 | 2163957.8163
| mechanical: pipework | 15% | of total A1 | 1298374.6898 | 0 | 0 | 0 | 0 | 0 | 1298374.6898 | 1298374.6898
| Total mechanical cost (total A1) | 50% | of total A2 | 8655831.2651 | 0 | 0 | 0 | 0 | 0 | 8655831.2651
| Total electrical cost | 20% | of total A2 | 3462332.506 | 0 | 0 | 0 | 0 | 0 | 3462332.506 | 3462332.506
| Total civil cost | 30% | of total A2 | 5193498.7591 | 0 | 0 | 0 | 0 | 0 | 5193498.7591 |  |  | 5193498.7591
| Subtotal: elec/mech/civil cost (total A2) |  |  | 17311662.5302 | 0 | 0 | 0 | 0 | 0 | 17311662.5302
| access road cost | R/km | 3000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| forebay | R/m3 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Subtotal: (total A3) |  |  | 17311662.5302 | 0 | 0 | 0 | 0 | 0 | 17311662.5302 | 6924665.0121 | 5193498.7591 | 5193498.7591 |  | 17311662.5302
| landscaping |  | 5% | 865583.1265 | 0 | 0 | 0 | 0 | 0 | 865583.1265 | 0 | 0 | 865583.1265
| miscellaneous |  | 10% | 1731166.253 | 0 | 0 | 0 | 0 | 0 | 1731166.253 | 0 | 0 | 1731166.253
| Subtotal: (total A) |  |  | 19908411.9098 | 0 | 0 | 0 | 0 | 0 | 19908411.9098 | 6924665.0121 | 5193498.7591 | 7790248.1386 |  | 19908411.9098
| Preliminary and General |  | 30% | 5972523.5729 | 0 | 0 | 0 | 0 | 0 | 5972523.5729 | 2077399.5036 | 1558049.6277 | 2337074.4416
| Preliminary Work |  |  | 455692.7401 | 0 | 0 | 0 | 0 | 0 | 455692.7401 | 0 | 0 | 455692.7401
| Subtotal: (total B) |  |  | 26336628.2229 | 0 | 0 | 0 | 0 | 0 | 26336628.2229 | 9002064.5157 | 6751548.3868 | 10583015.3203 |  | 26336628.2229
| Contingencies |  | 20% | 5267325.6446 | 0 | 0 | 0 | 0 | 0 | 5267325.6446 | 1800412.9031 | 1350309.6774 | 2116603.0641
| Subtotal: (total C) |  |  | 31603953.8674 | 0 | 0 | 0 | 0 | 0 | 31603953.8674 | 10802477.4189 | 8101858.0642 | 12699618.3844 |  | 31603953.8674
| Planning, design and supervision fees |  | 15% | 4740593.0801 | 0 | 0 | 0 | 0 | 0 | 4740593.0801 | 1620371.6128 | 1215278.7096 | 1904942.7577
| Total cost excluding VAT (total D) |  |  | 36344546.9475 | 0 | 0 | 0 | 0 | 0 | 36344546.9475 | 12422849.0317 | 9317136.7738 | 14604561.1421 |  | 36344546.9475
| Cost of ESKOM transmission lines to site |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Connection fee |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value Added Tax |  | 14% | 5088236.5727 | 0 | 0 | 0 | 0 | 0 | 5088236.5727 | 1739198.8644 | 1304399.1483 | 2044638.5599 | 0 | 5088236.5727
| Relocations and land acquisition |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
| Total cost including VAT |  |  | 41432783.5202 | 0 | 0 | 0 | 0 | 0 | 41432783.5202 | 14162047.8961 | 10621535.9221 | 16649199.702 | 0 | 41432783.5202
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
ANNUAL COST OF ELECTRICITY (24 h operation)
| Network Access Charge |  |  | 114969.454 | 0 | 0 | 0 | 0 | 0 | 114969.454
| Network Demand Charge |  |  | 67334.3635 | 0 | 0 | 0 | 0 | 0 | 67334.3635
| Reactive Energy Charge |  |  | 48377.944 | 0 | 0 | 0 | 0 | 0 | 48377.944
| Voltage Surcharge |  |  | 193919.7037 | 0 | 0 | 0 | 0 | 0 | 193919.7037
| Annual energy Cost (R/MWh) |  | 173.336 | 1580602.5797 | 0 | 0 | 0 | 0 | 0 | 1580602.5797
| Service & Admin Charge |  |  | 48055.9 | 0 | 0 | 0 | 0 | 0 | 48055.9
| Total annual cost |  |  | 2053259.9449 | 0 | 0 | 0 | 0 | 0 | 2053259.9449
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
| DESCRIPTION |  | UNIT/RATE | P1 | P2 | P3 | P4 | P5 | P6 | TOTAL
RISING MAIN COST
| Pipeline |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Road, river and rail crossings
| (a) national & provincial road |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| (b) national & provincial road |  |  | #REF! | #REF! | #REF!
| (c) river |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| (d) rail |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total A |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| landscaping |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| miscellaneous |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total B |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| preliminary and general |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| preliminary works |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| accomodation |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total C |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| contingencies |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total D |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| planning, design and supervision |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total E |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| VAT |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Relocations and land acquisition |  |  | #REF! | #REF! |  |  |  |  | #REF!
| Total cost including VAT |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  |  | 140 | 50 | 50
Note on B61: User: Power required at duty
Note on B62: User: Power absorbed at duty
Note on B63: User: Power absorbed at installed
Note on B66: User: Power required at peak operating

## Base Data
Name | Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Option | Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
Rates: | April 2008
Base Year | 2008
1. Energy charge |  |  |  | Note: All the shaded cells might be changed
Megaflex
Rates excl VAT
| Rate: c/kWh (incl. rural subsidy) |  |  |  |  | Energy charge - weekly allocation for 24 hr pumping
Rate | Summer | Winter |  |  | Pumping hours | 24
High | 23.22 | 76.37 |  |  | High | 25
Standard | 15.23 | 21.78 |  |  | Standard | 62
Off peak | 11.42 | 12.83 |  |  | Off Peak | 81
[5 empty] | Check Sum | 24
Months per season | 9 | 3
Weighted Average cost of energy (c/kWh)
| Energy charge daily rate allocation - Megaflex |  |  |  |  | c/kWh | R/MWh
| Weekdays | Saturday | Sunday |  | Pumping hours | 24 | 24
High | 5 | 0 | 0 |  | Cost per week | 2912.045
Standard | 11 | 7 | 0 |  | Cost per day | 416.0064
Off Peak | 8 | 17 | 24 |  | Cost per hr | 17.3336 | 173.336
Other Costs (R/day) | Daily charge | Monthly cost | Once off cost
Service & Admin charge | 131.66 |  |  |  | Note: Charged per account |  | Must confirm if per PS site, or one for total scheme
Network Access Charge (R/kVa) |  | 8.4 |  |  | Note: Applicable during all time periods | [6 empty] | 100.8
Network Demand Charge (R/kVA/month) |  | 9.5 |  |  | Note: Payable for each kVA supplied during peak and standard periods | [6 empty] | 114
Reactive Energy Charge (R/kVaRh) |  | 0.0374 |  |  | Note: applied to portion supplied in excess of 30% of kWh recorded during peak and standard periods
Voltage Surcharge |  | 11% |  |  | Note: Calculated as a percentage of network demand, network access and active energy charges. Includes for expected 25% increase in the Voltage surcharge (frpm 7.63%)
Connection Fee |  |  |  |  | Note: Case specific
Total yearly charges
2. Rates for discounting future costs & escalation of energy
Discount rates (real) (%/a) | 6 | 8 | 10
Escalation of energy (Yr) | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Yr6 | Yr7 | Yr8 | Yr9 | Yr10 |  |  |  |  | Energy Escalation Factors
Escalation of energy (real) (%/a) | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1.2 | 1.44 | 1.728 | 2.0736 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883 | 2.4883
Actual Year | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 |  |  |  |  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071
3. Setup defaults
Long Term Pipe roughness (epoxy lined) | 0.1 | (mm)
Max design flow velocity | 1.8 | m/s
Secondary losses | 0.25 | m/km
Steel pipe material yield | 290 | Mpa | Grade X42
Max allowable design stress | 50% | of yield
No of pipelines (1=single, 2 = parralel) | 1
Number of pumps | 4
Standby pumps | 1 |  | 25%
Efficiency of pump (Ep) | 90%
Efficiency of motor (Em) | 97%
Average loss in efficiency between major overhauls (Eo) | 1.5%
MW/MVA ratio (power factor Pf) | 0.96
Boschkop Weir Abstraction PS Elevation | 924 | masl | VKE (D v Coller): 11/08/2008
Boschkop Weir High Lift PS Elevation | 950 | masl | Based on 1:200 flood level provided by VKE + 10 m for pump sump to ensure free draining structure above 1:200 flood level
Vlieepoort Weir Abstraction PS Elevation | 885 | masl | VKE (D v Coller): 11/08/2008
Vlieepoort Weir High Lift PS | 920 | masl | Based on 1:200 flood level provided by VKE + 10 m for pump sump to ensure free draining structure above 1:200 flood level
Terminal Dams (max level) | 1044 | masl | Dam site 1 - max operating level as per Graham Simpson Email
Balancing Reservoir | 1015 | masl | Balancing Reservoir Node 15 Ground Level
Minimum residual head at destination | 15 | m
Annual Downtime (pumping system) | 18 | days | Based on reliability criteria |  | 347
Reliability design peak factor (pumping) | 1.0519 | fraction
Refill period | 347 | days
Emergency peak factor (max) | 1.0519 | fraction | Peak flow to fill storage in 20 days
Annual Downtime (gravity system) | 9 | days | Based on reliability criteria
Reliability design peak factor (gravity) | 1.0253 | fraction
Losses | 0 | % | Percentage of ave annual supply |  | Check VAPS Guideline
BOQ Items
Pipe Lay and join & fittings | 20% | of material cost | Peter to confirm
Landscaping/Env remediation | 5% |  | Peter to comment
Miscellaneous | 10% |  | Peter to comment
P&G's | 30% |  | Peter to confirm
Contingencies | 20% |  | Peter to confirm
Planning Design & Supervision | 15% |  | Peter to confirm
Width of permanent servitude | 20 | m
Width of construction servitude | 30 | m
Trench Geometry
Side Allowance | 500 | mm | for D up to 2000
| 600 |  | for D > 2000
Bedding thickness | 300 | mm
Selected Fill Over Pipe | 300 | mm
Batter angle (from vertical) | 15 | deg | Geotech guys to confirm
Min Cover | 1300 | mm | for D up to 1500
| 1800 |  | for D > 1500
% Hard Excvation | 40% |  | Geotech guys to confirm
% Bedding from trench | 30% |  | Geotech guys to confirm
% Bedding Cradle & Fill blanket from trench | 30% |  | Geotech guys to confirm
Maintenance Requirements
Major overhaul every 15 years: | 15% | of initial capital cost of pump and motor
Maintenance cost (mechanical & electrical) | 4% | of electrical/mechanical cost
Maintenance cost (pumpstation civil) | 0.25% | of civil cost
Maintenance cost (pipelines) | 0.5% | of pipeline cost
4. Demand Projection for the calculation of the energy costs
YEAR | NET DEMAND | LOSSES % | GROSS DEMAND | PUMP RATE 347 days |  | Raw Water Demands | Raw Water Demands | Losses to be Augmented from Crocodile Scheme |  | Interim scheme needs to deliver full demand up to 2014
| million m3/yr |  | million m3/yr | m3/s
Demand
[6 empty] | @ River Bend Weir | @ Mokolo Dam | Weir - Dam |  | 2008 | 2009 | 2010 | 2011 | 2012 | 2008: 2013; 2009: 2014
2008 | 0 | 0% | 0 | 0 |  | 15.4986 | 12.6211 | 2.8775 |  | 12.131 | 13.7474 | 14.5972 | 20.2522 | 28.0254 | 2008: 39.6285; 2009: 50.4025
2009 | 0 | 0% | 0 | 0 |  | 17.5637 | 14.3027 | 3.2609
2010 | 0 | 0% | 0 | 0 |  | 18.6495 | 15.187 | 3.4625 |  | Interim 2014 Demand | 50.402
2011 | 20.2522 | 2% | 20.6655 | 0.68929 |  | 25.8743 | 21.0704 | 4.8039 |  | Existing Mokolo Pipe | 13.5
2012 | 28.0254 | 2% | 28.5974 | 0.95386 |  | 35.8054 | 29.1577 | 6.6477 |  | Add Req for Interim | 36.902
2013 | 36.7 | 2% | 37.449 | 1.2491 |  | 50.6295 | 41.2295 | 9.4
2014 | 36.7 | 2% | 37.449 | 1.2491 |  | 46.5201 | 37.883 | 8.637 |  | Notes:
2015 | 27.4 | 2% | 27.9592 | 0.93257 |  | 35.0063 | 28.507 | 6.4994
2016 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  | Max shortterm demand through new pipes |  | 36.902 | million m3/yr
2017 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  | Longterm Yield from Mokolo Dam |  | 28.7 | million m3/yr
2018 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  | Capacity of Existing Pipeline |  | 13.5 | million m3/yr
2019 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  | Required longterm delivery of new pipeline |  | 15.2 | million m3/yr
2020 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2021 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2022 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  | Assumption: | * The existing pipeline will continue to deliver water at its current capacity.
2023 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2024 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  |  | * The new pipeline from Mokolo Dam/Weir will deliver only the additional
2025 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  |  | demand from the dam/weir.
2026 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2027 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  |  | * The remaining capactity of the pipes and pumps will be seen as back-up capacity.
2028 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2029 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  | Therefore the demand through the pipeline from the Mokolo Dam/Weir which was built as
2030 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077 |  | an interim scheme, will be 15.2 Mm3/a.
2031 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2032 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2033 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2034 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2035 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2036 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2037 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2038 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2039 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2040 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2041 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2042 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2043 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2044 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2045 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2046 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2047 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2048 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2049 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2050 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2051 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2052 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2053 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2054 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
2055 | 28.7 | 2% | 29.2857 | 0.97682 |  | 36.6672 | 29.8595 | 6.8077
Max pumping rate (m^3/s) |  |  |  | 1.2491
Design velocity (m/s) |  |  |  | 1.8
Indicative pipe diameter for URV assessment |  |  |  | 900
Emergency peak flow |  |  |  | 1.2491
Flow velocity at EPF |  |  |  | 1.9635
Diameter selected for analysis |  |  |  | 2200
4. Methodology
Note on B113: njordaan: Pipelines were designed for 36.9 Mm3/a, but the max demand = 36.7Mm3/a.
Note on B115: njordaan: In 2015 the existing pipeline will be refurbished and the entire water requirement will be pumped along the new pipeline.
Note on G107: njordaan: These are the gross water requirements provided by Johan Pienaar 03-11-2008 for URV calculation purposes. Used these figures only to determine the cost of the raw water in the Economic Model. Still used our requirement figures in Pump Model.
Note on H107: njordaan: These are the gross water requirements provided by Johan Pienaar 03-11-2008 for URV calculation purposes. Used these figures only to determine the cost of the raw water in the Economic Model. Still used our requirement figures in Pump Model.
300
D
D/2
D/2
Min Cover
Side
300
ø

## Hydr Assessment
[7 empty] | System parameters |  |  |  |  | Pumping System
[7 empty] | Pipe roughness | 0.1 | (mm) |  |  |  | PS Head | Start Ch | Start Elev | End Ch | End Elev | Static Diff
[7 empty] | Boschkop Weir High Lift Elevation | 950 | masl |  |  | Section 1 | 260 | 0 | 920 | 111347.709 | 1041.736 | 121.736
[7 empty] | Vlieepoort Weir High Lift | 920 | masl |  |  | Section 2 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Terminal Dams (max level) | 1044 | masl |  |  | Section 3 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Balancing Res | 1015 | masl
[7 empty] | Losses | 0.00025 | m/m |  |  | Check |  |  | 105.2754 |  | Minimum value = 15 |  |  | 15
[7 empty] | Design Flow | 1.2491 | m^3/s
[7 empty] | Pipe Dia | 2200 | mm
Node #1 | Node #2 | Length (m) | Node Number | Chainage (m) | Elevation (m) | Notes | Nom Dia | ID | OD | Flow rate (m^3/s) | Flow velocity (m/s) | ks (m) | Lambda | Head loss | Secondary loss | Total Headloss | Add Pumping Head | HGL (m) | Head (m)
Node 7 | 0 | 0.122 | Node 7 | 0 | 920 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 3.1639e-06 | 3.05e-05 | 3.3664e-05 | 260 | 1180 | 260
0 | 0 | 129.881 | 0 | 0.122 | 900.562 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0033683 | 0.03247 | 0.035839 |  | 1180 | 279.438
0 | 0 | 46.29 | 0 | 130.003 | 904.74 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0012005 | 0.011572 | 0.012773 |  | 1179.9641 | 275.2241
0 | 0 | 25.489 | 0 | 176.293 | 905.93 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00066103 | 0.0063723 | 0.0070333 |  | 1179.9514 | 274.0214
0 | 0 | 105.071 | 0 | 201.782 | 905.17 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0027249 | 0.026268 | 0.028993 |  | 1179.9443 | 274.7743
0 | 0 | 64.806 | 0 | 306.853 | 905.518 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0016807 | 0.016202 | 0.017882 |  | 1179.9153 | 274.3973
0 | 0 | 125.828 | 0 | 371.659 | 899.404 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0032632 | 0.031457 | 0.03472 |  | 1179.8974 | 280.4934
0 | 0 | 38.709 | 0 | 497.487 | 899.89 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010039 | 0.0096773 | 0.010681 |  | 1179.8627 | 279.9727
0 | 0 | 131.223 | 0 | 536.196 | 900.905 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0034031 | 0.032806 | 0.036209 |  | 1179.852 | 278.947
0 | 0 | 76.653 | 0 | 667.419 | 904.593 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0019879 | 0.019163 | 0.021151 |  | 1179.8158 | 275.2228
0 | 0 | 150.479 | 0 | 744.072 | 910.018 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0039025 | 0.03762 | 0.041522 |  | 1179.7947 | 269.7767
0 | 0 | 1.694 | 0 | 894.551 | 924.264 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 4.3932e-05 | 0.0004235 | 0.00046743 |  | 1179.7532 | 255.4892
0 | 0 | 64.717 | 0 | 896.245 | 924.424 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0016784 | 0.016179 | 0.017858 |  | 1179.7527 | 255.3287
0 | 0 | 39.898 | 0 | 960.962 | 922.678 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010347 | 0.0099745 | 0.011009 |  | 1179.7348 | 257.0568
0 | 0 | 23.175 | 0 | 1000.86 | 914.897 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00060102 | 0.0057938 | 0.0063948 |  | 1179.7238 | 264.8268
0 | 0 | 196.927 | 0 | 1024.035 | 914.757 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0051071 | 0.049232 | 0.054339 |  | 1179.7174 | 264.9604
0 | 0 | 72.386 | 0 | 1220.962 | 920.298 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0018773 | 0.018097 | 0.019974 |  | 1179.6631 | 259.3651
0 | 0 | 61.746 | 0 | 1293.348 | 925.463 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0016013 | 0.015437 | 0.017038 |  | 1179.6431 | 254.1801
0 | 0 | 112.283 | 0 | 1355.094 | 924.539 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0029119 | 0.028071 | 0.030983 |  | 1179.6261 | 255.0871
0 | 0 | 28.098 | 0 | 1467.377 | 920.981 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00072869 | 0.0070245 | 0.0077532 |  | 1179.5951 | 258.6141
0 | 0 | 118.338 | 0 | 1495.475 | 920.228 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.003069 | 0.029584 | 0.032653 |  | 1179.5873 | 259.3593
0 | 0 | 26.308 | 0 | 1613.813 | 920.444 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00068227 | 0.006577 | 0.0072593 |  | 1179.5547 | 259.1107
0 | 0 | 102.396 | 0 | 1640.121 | 919.858 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0026555 | 0.025599 | 0.028255 |  | 1179.5474 | 259.6894
0 | 0 | 140.976 | 0 | 1742.517 | 917.576 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0036561 | 0.035244 | 0.0389 |  | 1179.5192 | 261.9432
0 | 0 | 76.335 | 0 | 1883.493 | 914.81 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0019797 | 0.019084 | 0.021063 |  | 1179.4803 | 264.6703
0 | 0 | 52.968 | 0 | 1959.828 | 914.322 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0013737 | 0.013242 | 0.014616 |  | 1179.4592 | 265.1372
0 | 0 | 372.358 | 0 | 2012.796 | 914.971 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0096567 | 0.09309 | 0.10275 |  | 1179.4446 | 264.4736
0 | 0 | 349.319 | 0 | 2385.154 | 913.716 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0090592 | 0.08733 | 0.096389 |  | 1179.3419 | 265.6259
0 | 0 | 216.741 | 0 | 2734.473 | 911.156 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0056209 | 0.054185 | 0.059806 |  | 1179.2455 | 268.0895
0 | 0 | 6.081 | 0 | 2951.214 | 911.23 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0001577 | 0.0015203 | 0.001678 |  | 1179.1857 | 267.9557
0 | 0 | 234.037 | 0 | 2957.295 | 911.224 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0060695 | 0.058509 | 0.064579 |  | 1179.184 | 267.96
0 | 0 | 187.093 | 0 | 3191.332 | 920.153 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0048521 | 0.046773 | 0.051625 |  | 1179.1194 | 258.9664
0 | 0 | 283.788 | 0 | 3378.425 | 925.919 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0073597 | 0.070947 | 0.078307 |  | 1179.0678 | 253.1488
0 | 0 | 228.433 | 0 | 3662.213 | 940.221 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0059242 | 0.057108 | 0.063032 |  | 1178.9895 | 238.7685
0 | 0 | 361.972 | 0 | 3890.646 | 943.211 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0093873 | 0.090493 | 0.09988 |  | 1178.9264 | 235.7154
0 | 0 | 261.4 | 0 | 4252.618 | 951.325 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0067791 | 0.06535 | 0.072129 |  | 1178.8266 | 227.5016
0 | 0 | 261.858 | 0 | 4514.018 | 956.055 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.006791 | 0.065465 | 0.072256 |  | 1178.7544 | 222.6994
0 | 0 | 67.692 | 0 | 4775.876 | 962.462 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0017555 | 0.016923 | 0.018679 |  | 1178.6822 | 216.2202
0 | 0 | 105.686 | 0 | 4843.568 | 964.881 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0027409 | 0.026421 | 0.029162 |  | 1178.6635 | 213.7825
0 | 0 | 61.445 | 0 | 4949.254 | 966.308 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0015935 | 0.015361 | 0.016955 |  | 1178.6343 | 212.3263
0 | 0 | 78.401 | 0 | 5010.699 | 968.188 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0020332 | 0.0196 | 0.021633 |  | 1178.6174 | 210.4294
0 | 0 | 110.377 | 0 | 5089.1 | 968.881 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0028625 | 0.027594 | 0.030457 |  | 1178.5957 | 209.7147
0 | 0 | 314.015 | 0 | 5199.477 | 971.067 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0081436 | 0.078504 | 0.086647 |  | 1178.5653 | 207.4983
0 | 0 | 107.419 | 0 | 5513.492 | 979.848 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0027858 | 0.026855 | 0.029641 |  | 1178.4786 | 198.6306
0 | 0 | 223.696 | 0 | 5620.911 | 984.794 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0058013 | 0.055924 | 0.061725 |  | 1178.449 | 193.655
0 | 0 | 16.98 | 0 | 5844.607 | 999.648 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00044036 | 0.004245 | 0.0046854 |  | 1178.3873 | 178.7393
0 | 0 | 2.575 | 0 | 5861.587 | 1003.328 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 6.678e-05 | 0.00064375 | 0.00071053 |  | 1178.3826 | 175.0546
0 | 0 | 141.92 | 0 | 5864.162 | 1003.884 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0036805 | 0.03548 | 0.039161 |  | 1178.3819 | 174.4979
0 | 0 | 96.801 | 0 | 6006.082 | 1004.081 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0025104 | 0.0242 | 0.026711 |  | 1178.3427 | 174.2617
0 | 0 | 138.163 | 0 | 6102.883 | 1001.238 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0035831 | 0.034541 | 0.038124 |  | 1178.316 | 177.078
0 | 0 | 168.325 | 0 | 6241.046 | 1000.7 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0043653 | 0.042081 | 0.046447 |  | 1178.2779 | 177.5779
0 | 0 | 53.866 | 0 | 6409.371 | 998.493 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.001397 | 0.013466 | 0.014863 |  | 1178.2314 | 179.7384
0 | 0 | 46.284 | 0 | 6463.237 | 997.462 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0012003 | 0.011571 | 0.012771 |  | 1178.2166 | 180.7546
0 | 0 | 3.904 | 0 | 6509.521 | 995.265 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00010125 | 0.000976 | 0.0010772 |  | 1178.2038 | 182.9388
0 | 0 | 154.548 | 0 | 6513.425 | 995.119 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.004008 | 0.038637 | 0.042645 |  | 1178.2027 | 183.0837
0 | 0 | 25.229 | 0 | 6667.973 | 1012.96 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00065429 | 0.0063073 | 0.0069615 |  | 1178.1601 | 165.2001
0 | 0 | 37.809 | 0 | 6693.202 | 1016.898 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00098054 | 0.0094523 | 0.010433 |  | 1178.1531 | 161.2551
0 | 0 | 86.576 | 0 | 6731.011 | 1021.034 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0022453 | 0.021644 | 0.023889 |  | 1178.1427 | 157.1087
0 | 0 | 8.833 | 0 | 6817.587 | 1020.216 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00022907 | 0.0022082 | 0.0024373 |  | 1178.1188 | 157.9028
0 | 0 | 22.932 | 0 | 6826.42 | 1020.208 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00059472 | 0.005733 | 0.0063277 |  | 1178.1164 | 157.9084
0 | 0 | 12.578 | 0 | 6849.352 | 1020.817 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0003262 | 0.0031445 | 0.0034707 |  | 1178.11 | 157.293
0 | 0 | 28.71 | 0 | 6861.93 | 1019.673 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00074456 | 0.0071775 | 0.0079221 |  | 1178.1066 | 158.4336
0 | 0 | 107.019 | 0 | 6890.64 | 1014.464 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0027754 | 0.026755 | 0.02953 |  | 1178.0986 | 163.6346
0 | 0 | 11.176 | 0 | 6997.659 | 1000.875 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00028984 | 0.002794 | 0.0030838 |  | 1178.0691 | 177.1941
0 | 0 | 2.987 | 0 | 7008.835 | 1000.638 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 7.7465e-05 | 0.00074675 | 0.00082421 |  | 1178.066 | 177.428
0 | 0 | 63.944 | 0 | 7011.822 | 999.725 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0016583 | 0.015986 | 0.017644 |  | 1178.0652 | 178.3402
0 | 0 | 97.002 | 0 | 7075.766 | 992.873 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0025156 | 0.024251 | 0.026766 |  | 1178.0476 | 185.1746
0 | 0 | 60.175 | 0 | 7172.768 | 983.399 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0015606 | 0.015044 | 0.016604 |  | 1178.0208 | 194.6218
0 | 0 | 28.97 | 0 | 7232.943 | 980.201 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00075131 | 0.0072425 | 0.0079938 |  | 1178.0042 | 197.8032
0 | 0 | 109.633 | 0 | 7261.913 | 978.785 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0028432 | 0.027408 | 0.030251 |  | 1177.9962 | 199.2112
0 | 0 | 23.806 | 0 | 7371.546 | 974.841 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00061738 | 0.0059515 | 0.0065689 |  | 1177.9659 | 203.1249
0 | 0 | 303.798 | 0 | 7395.352 | 974.402 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0078787 | 0.07595 | 0.083828 |  | 1177.9594 | 203.5574
0 | 0 | 182.252 | 0 | 7699.15 | 970.345 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0047265 | 0.045563 | 0.05029 |  | 1177.8755 | 207.5305
0 | 0 | 11.172 | 0 | 7881.402 | 969.406 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00028973 | 0.002793 | 0.0030827 |  | 1177.8253 | 208.4193
0 | 0 | 152.716 | 0 | 7892.574 | 969.423 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0039605 | 0.038179 | 0.04214 |  | 1177.8222 | 208.3992
0 | 0 | 451.263 | 0 | 8045.29 | 969.635 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.011703 | 0.11282 | 0.12452 |  | 1177.78 | 208.145
0 | 0 | 262.115 | 0 | 8496.553 | 967.668 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0067977 | 0.065529 | 0.072326 |  | 1177.6555 | 209.9875
0 | 0 | 52.348 | 0 | 8758.668 | 965.038 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0013576 | 0.013087 | 0.014445 |  | 1177.5832 | 212.5452
0 | 0 | 181.581 | 0 | 8811.016 | 963.821 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0047091 | 0.045395 | 0.050104 |  | 1177.5687 | 213.7477
0 | 0 | 98.525 | 0 | 8992.597 | 959.715 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0025551 | 0.024631 | 0.027186 |  | 1177.5186 | 217.8036
0 | 0 | 20.631 | 0 | 9091.122 | 959.532 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00053504 | 0.0051578 | 0.0056928 |  | 1177.4915 | 217.9595
0 | 0 | 318.061 | 0 | 9111.753 | 959.729 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0082486 | 0.079515 | 0.087764 |  | 1177.4858 | 217.7568
0 | 0 | 15.031 | 0 | 9429.814 | 963.248 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00038981 | 0.0037577 | 0.0041476 |  | 1177.398 | 214.15
0 | 0 | 412.011 | 0 | 9444.845 | 963.395 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.010685 | 0.103 | 0.11369 |  | 1177.3938 | 213.9988
0 | 0 | 161.6 | 0 | 9856.856 | 964.853 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0041909 | 0.0404 | 0.044591 |  | 1177.2802 | 212.4272
0 | 0 | 212.107 | 0 | 10018.456 | 966.711 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0055008 | 0.053027 | 0.058528 |  | 1177.2356 | 210.5246
0 | 0 | 200.635 | 0 | 10230.563 | 970.356 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0052032 | 0.050159 | 0.055362 |  | 1177.177 | 206.821
0 | 0 | 7.611 | 0 | 10431.198 | 969.955 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00019738 | 0.0019027 | 0.0021001 |  | 1177.1217 | 207.1667
0 | 0 | 118.187 | 0 | 10438.809 | 969.889 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0030651 | 0.029547 | 0.032612 |  | 1177.1196 | 207.2306
0 | 0 | 78.523 | 0 | 10556.996 | 967.959 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0020364 | 0.019631 | 0.021667 |  | 1177.087 | 209.128
0 | 0 | 345.232 | 0 | 10635.519 | 966.842 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0089532 | 0.086308 | 0.095261 |  | 1177.0653 | 210.2233
0 | 0 | 988.71 | 0 | 10980.751 | 964.601 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.025641 | 0.24718 | 0.27282 |  | 1176.97 | 212.369
0 | 0 | 339.798 | 0 | 11969.461 | 960.505 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0088123 | 0.08495 | 0.093762 |  | 1176.6972 | 216.1922
0 | 0 | 518.54 | 0 | 12309.259 | 960.303 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013448 | 0.12964 | 0.14308 |  | 1176.6035 | 216.3005
0 | 0 | 999.774 | 0 | 12827.799 | 956.32 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.025928 | 0.24994 | 0.27587 |  | 1176.4604 | 220.1404
0 | 0 | 325.353 | 0 | 13827.573 | 951.23 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0084377 | 0.081338 | 0.089776 |  | 1176.1845 | 224.9545
0 | 0 | 861.595 | 0 | 14152.926 | 948.633 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.022345 | 0.2154 | 0.23774 |  | 1176.0947 | 227.4617
0 | 0 | 128.984 | 0 | 15014.521 | 944.107 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0033451 | 0.032246 | 0.035591 |  | 1175.857 | 231.75
0 | Node 9 | 526.326 | 0 | 15143.505 | 943.818 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.01365 | 0.13158 | 0.14523 |  | 1175.8214 | 232.0034
Node 9 | Node 9 | 0 | Node 9 | 15669.831 | 942.423 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0 | 0 | 0 |  | 1175.6762 | 233.2532
Node 9 | 0 | 788.124 | Node 9 | 15669.831 | 942.423 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.020439 | 0.19703 | 0.21747 |  | 1175.6762 | 233.2532
0 | 0 | 789.061 | 0 | 16457.955 | 948.095 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.020463 | 0.19727 | 0.21773 |  | 1175.4587 | 227.3637
0 | 0 | 674.487 | 0 | 17247.016 | 952.03 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.017492 | 0.16862 | 0.18611 |  | 1175.241 | 223.211
0 | 0 | 397.774 | 0 | 17921.503 | 953.504 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.010316 | 0.099444 | 0.10976 |  | 1175.0548 | 221.5508
0 | 0 | 449.799 | 0 | 18319.277 | 953.532 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.011665 | 0.11245 | 0.12411 |  | 1174.9451 | 221.4131
0 | 0 | 1884.568 | 0 | 18769.076 | 959.654 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.048874 | 0.47114 | 0.52002 |  | 1174.821 | 215.167
0 | 0 | 1673.94 | 0 | 20653.644 | 972.143 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.043412 | 0.41848 | 0.4619 |  | 1174.301 | 202.158
0 | 0 | 23.481 | 0 | 22327.584 | 978.815 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00060895 | 0.0058702 | 0.0064792 |  | 1173.8391 | 195.0241
0 | 0 | 450.206 | 0 | 22351.065 | 978.926 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.011676 | 0.11255 | 0.12423 |  | 1173.8326 | 194.9066
0 | 0 | 1857.963 | 0 | 22801.271 | 981.863 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.048184 | 0.46449 | 0.51267 |  | 1173.7084 | 191.8454
0 | 0 | 441.511 | 0 | 24659.234 | 997.372 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.01145 | 0.11038 | 0.12183 |  | 1173.1957 | 175.8237
0 | 0 | 1267.983 | 0 | 25100.745 | 1000.256 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.032884 | 0.317 | 0.34988 |  | 1173.0739 | 172.8179
0 | 0 | 239.966 | 0 | 26368.728 | 1017.216 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0062233 | 0.059992 | 0.066215 |  | 1172.724 | 155.508
0 | 0 | 348.809 | 0 | 26608.694 | 1018.962 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.009046 | 0.087202 | 0.096248 |  | 1172.6578 | 153.6958
0 | 0 | 154.731 | 0 | 26957.503 | 1019.922 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0040128 | 0.038683 | 0.042696 |  | 1172.5615 | 152.6395
0 | 0 | 618.928 | 0 | 27112.234 | 1021.561 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.016051 | 0.15473 | 0.17078 |  | 1172.5188 | 150.9578
0 | 0 | 464.198 | 0 | 27731.162 | 1031.367 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.012038 | 0.11605 | 0.12809 |  | 1172.348 | 140.981
0 | 0 | 364.897 | 0 | 28195.36 | 1037.686 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0094632 | 0.091224 | 0.10069 |  | 1172.2199 | 134.5339
0 | 0 | 1025.47 | 0 | 28560.257 | 1041.736 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.026594 | 0.25637 | 0.28296 | 0 | 1172.1193 | 130.3833
0 | 0 | 285.293 | 0 | 29585.727 | 1056.872 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0073988 | 0.071323 | 0.078722 |  | 1171.8363 | 114.9643
0 | 0 | 182.761 | 0 | 29871.02 | 1060.002 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0047397 | 0.04569 | 0.05043 |  | 1171.7576 | 111.7556
0 | 0 | 335.744 | 0 | 30053.781 | 1062.015 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0087072 | 0.083936 | 0.092643 |  | 1171.7071 | 109.6921
0 | 0 | 714.892 | 0 | 30389.525 | 1066.722 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.01854 | 0.17872 | 0.19726 |  | 1171.6145 | 104.8925
0 | 0 | 1168.778 | 0 | 31104.417 | 1079.384 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.030311 | 0.29219 | 0.32251 |  | 1171.4172 | 92.0332
0 | 0 | 226.609 | 0 | 32273.195 | 1093.538 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0058769 | 0.056652 | 0.062529 |  | 1171.0947 | 77.5567
0 | 0 | 51.707 | 0 | 32499.804 | 1097.802 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.001341 | 0.012927 | 0.014268 |  | 1171.0322 | 73.2302
0 | 0 | 8.17 | 0 | 32551.511 | 1100.086 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00021188 | 0.0020425 | 0.0022544 |  | 1171.0179 | 70.9319
0 | 0 | 223.717 | 0 | 32559.681 | 1099.927 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0058019 | 0.055929 | 0.061731 |  | 1171.0157 | 71.0887
0 | 0 | 26.879 | 0 | 32783.398 | 1093.858 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00069708 | 0.0067198 | 0.0074168 |  | 1170.9539 | 77.0959
0 | 0 | 182.797 | 0 | 32810.277 | 1093.604 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0047406 | 0.045699 | 0.05044 |  | 1170.9465 | 77.3425
0 | 0 | 7.573 | 0 | 32993.074 | 1091.154 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0001964 | 0.0018932 | 0.0020896 |  | 1170.8961 | 79.7421
0 | 0 | 103.816 | 0 | 33000.647 | 1091.101 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0026924 | 0.025954 | 0.028646 |  | 1170.894 | 79.793
0 | 0 | 55.357 | 0 | 33104.463 | 1091.215 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0014356 | 0.013839 | 0.015275 |  | 1170.8654 | 79.6504
0 | 0 | 77.96 | 0 | 33159.82 | 1091.3 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0020218 | 0.01949 | 0.021512 |  | 1170.8501 | 79.5501
0 | 0 | 3.528 | 0 | 33237.78 | 1090.366 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 9.1495e-05 | 0.000882 | 0.00097349 |  | 1170.8286 | 80.4626
0 | 0 | 154.692 | 0 | 33241.308 | 1090.397 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0040118 | 0.038673 | 0.042685 |  | 1170.8276 | 80.4306
0 | 0 | 2.002 | 0 | 33396 | 1091.175 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 5.192e-05 | 0.0005005 | 0.00055242 |  | 1170.7849 | 79.6099
0 | 0 | 154.879 | 0 | 33398.002 | 1091.2 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0040166 | 0.03872 | 0.042736 |  | 1170.7844 | 79.5844
0 | 0 | 155.618 | 0 | 33552.881 | 1092.966 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0040358 | 0.038905 | 0.04294 |  | 1170.7416 | 77.7756
0 | 0 | 118.374 | 0 | 33708.499 | 1094.13 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0030699 | 0.029593 | 0.032663 |  | 1170.6987 | 76.5687
0 | 0 | 57.58 | 0 | 33826.873 | 1095.235 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0014933 | 0.014395 | 0.015888 |  | 1170.666 | 75.431
0 | 0 | 378.924 | 0 | 33884.453 | 1095.525 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.009827 | 0.094731 | 0.10456 |  | 1170.6501 | 75.1251
0 | 0 | 621.803 | 0 | 34263.377 | 1097.438 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.016126 | 0.15545 | 0.17158 |  | 1170.5456 | 73.1076
0 | 0 | 89.986 | 0 | 34885.18 | 1097.944 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0023337 | 0.022497 | 0.02483 |  | 1170.374 | 72.43
0 | 0 | 81.792 | 0 | 34975.166 | 1097.693 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0021212 | 0.020448 | 0.022569 |  | 1170.3492 | 72.6562
0 | 0 | 121.17 | 0 | 35056.958 | 1097.399 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0031424 | 0.030292 | 0.033435 |  | 1170.3266 | 72.9276
0 | 0 | 619.612 | 0 | 35178.128 | 1096.31 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.016069 | 0.1549 | 0.17097 |  | 1170.2932 | 73.9832
0 | 0 | 25.071 | 0 | 35797.74 | 1088.836 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00065019 | 0.0062678 | 0.0069179 |  | 1170.1222 | 81.2862
0 | 0 | 507.676 | 0 | 35822.811 | 1088.495 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013166 | 0.12692 | 0.14009 |  | 1170.1153 | 81.6203
0 | 0 | 509.722 | 0 | 36330.487 | 1080.479 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013219 | 0.12743 | 0.14065 |  | 1169.9752 | 89.4962
0 | Node 10 | 359.099 | 0 | 36840.209 | 1077.671 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0093128 | 0.089775 | 0.099088 |  | 1169.8345 | 92.1635
Node 10 | Node 10 | 0 | Node 10 | 37199.308 | 1078.31 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0 | 0 | 0 |  | 1169.7354 | 91.4254
Node 10 | 0 | 0.051 | Node 10 | 37199.308 | 1078.31 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 1.3226e-06 | 1.275e-05 | 1.4073e-05 |  | 1169.7354 | 91.4254
0 | 0 | 187.472 | 0 | 37199.359 | 1078.31 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0048619 | 0.046868 | 0.05173 |  | 1169.7354 | 91.4254
0 | 0 | 623.35 | 0 | 37386.831 | 1079.306 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.016166 | 0.15584 | 0.172 |  | 1169.6837 | 90.3777
0 | 0 | 967.145 | 0 | 38010.181 | 1080.295 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.025082 | 0.24179 | 0.26687 |  | 1169.5117 | 89.2167
0 | 0 | 2104.957 | 0 | 38977.326 | 1078.84 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.05459 | 0.52624 | 0.58083 |  | 1169.2448 | 90.4048
0 | 0 | 1076.632 | 0 | 41082.283 | 1070.814 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.027921 | 0.26916 | 0.29708 |  | 1168.664 | 97.85
0 | 0 | 327.122 | 0 | 42158.915 | 1067.962 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0084836 | 0.081781 | 0.090264 |  | 1168.3669 | 100.4049
0 | 0 | 1838.688 | 0 | 42486.037 | 1066.556 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.047684 | 0.45967 | 0.50736 |  | 1168.2767 | 101.7207
0 | 0 | 671.856 | 0 | 44324.725 | 1056.627 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.017424 | 0.16796 | 0.18539 |  | 1167.7693 | 111.1423
0 | 0 | 408.049 | 0 | 44996.581 | 1052.116 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.010582 | 0.10201 | 0.11259 |  | 1167.5839 | 115.4679
0 | 0 | 388.05 | 0 | 45404.63 | 1050.044 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.010064 | 0.097013 | 0.10708 |  | 1167.4713 | 117.4273
0 | 0 | 469.219 | 0 | 45792.68 | 1049.832 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.012169 | 0.1173 | 0.12947 |  | 1167.3642 | 117.5322
0 | 0 | 478.292 | 0 | 46261.899 | 1052.528 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.012404 | 0.11957 | 0.13198 |  | 1167.2348 | 114.7068
0 | 0 | 126.567 | 0 | 46740.191 | 1059.064 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0032824 | 0.031642 | 0.034924 |  | 1167.1028 | 108.0388
0 | 0 | 116.674 | 0 | 46866.758 | 1054.23 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0030258 | 0.029168 | 0.032194 |  | 1167.0679 | 112.8379
0 | 0 | 119.716 | 0 | 46983.432 | 1041.027 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0031047 | 0.029929 | 0.033034 |  | 1167.0357 | 126.0087
0 | 0 | 94.65 | 0 | 47103.148 | 1037.32 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0024546 | 0.023663 | 0.026117 |  | 1167.0026 | 129.6826
0 | 0 | 66.477 | 0 | 47197.798 | 1036.08 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.001724 | 0.016619 | 0.018343 |  | 1166.9765 | 130.8965
0 | 0 | 240.695 | 0 | 47264.275 | 1035.208 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0062422 | 0.060174 | 0.066416 |  | 1166.9582 | 131.7502
0 | 0 | 2049.648 | 0 | 47504.97 | 1033.38 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.053155 | 0.51241 | 0.56557 |  | 1166.8918 | 133.5118
0 | 0 | 3675.192 | 0 | 49554.618 | 1022.825 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.095312 | 0.9188 | 1.0141 |  | 1166.3262 | 143.5012
0 | 0 | 73.752 | 0 | 53229.81 | 1005.923 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0019127 | 0.018438 | 0.020351 |  | 1165.3121 | 159.3891
0 | 0 | 682.172 | 0 | 53303.562 | 1005.452 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.017691 | 0.17054 | 0.18823 |  | 1165.2917 | 159.8397
0 | 0 | 1276.769 | 0 | 53985.734 | 1000.873 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.033112 | 0.31919 | 0.3523 |  | 1165.1035 | 164.2305
0 | 0 | 219.635 | 0 | 55262.503 | 996.937 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.005696 | 0.054909 | 0.060605 |  | 1164.7512 | 167.8142
0 | 0 | 615.43 | 0 | 55482.138 | 996.462 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.015961 | 0.15386 | 0.16982 |  | 1164.6906 | 168.2286
0 | 0 | 30.241 | 0 | 56097.568 | 995.465 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00078427 | 0.0075603 | 0.0083445 |  | 1164.5208 | 169.0558
0 | 0 | 2679.098 | 0 | 56127.809 | 995.516 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.069479 | 0.66977 | 0.73925 |  | 1164.5124 | 168.9964
0 | 0 | 58.441 | 0 | 58806.907 | 1001.817 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0015156 | 0.01461 | 0.016126 |  | 1163.7732 | 161.9562
0 | 0 | 1984.463 | 0 | 58865.348 | 1001.881 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.051465 | 0.49612 | 0.54758 |  | 1163.7571 | 161.8761
0 | 0 | 1794.228 | 0 | 60849.811 | 1002.162 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.046531 | 0.44856 | 0.49509 |  | 1163.2095 | 161.0475
0 | 0 | 745.585 | 0 | 62644.039 | 997.769 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.019336 | 0.1864 | 0.20573 |  | 1162.7144 | 164.9454
0 | 0 | 405.699 | 0 | 63389.624 | 997.308 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.010521 | 0.10142 | 0.11195 |  | 1162.5087 | 165.2007
0 | 0 | 1138.785 | 0 | 63795.323 | 993.589 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.029533 | 0.2847 | 0.31423 |  | 1162.3967 | 168.8077
0 | 0 | 1565.146 | 0 | 64934.108 | 983.82 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.04059 | 0.39129 | 0.43188 |  | 1162.0825 | 178.2625
0 | 0 | 56.875 | 0 | 66499.254 | 975.602 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.001475 | 0.014219 | 0.015694 |  | 1161.6506 | 186.0486
0 | 0 | 2336.916 | 0 | 66556.129 | 975.479 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.060605 | 0.58423 | 0.64483 |  | 1161.6349 | 186.1559
0 | 0 | 2361.696 | 0 | 68893.045 | 974.07 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.061248 | 0.59042 | 0.65167 |  | 1160.9901 | 186.9201
0 | 0 | 1842.451 | 0 | 71254.741 | 959.929 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.047782 | 0.46061 | 0.50839 |  | 1160.3384 | 200.4094
0 | 0 | 1173.569 | 0 | 73097.192 | 956.465 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.030435 | 0.29339 | 0.32383 |  | 1159.83 | 203.365
0 | 0 | 81.141 | 0 | 74270.761 | 955.603 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0021043 | 0.020285 | 0.02239 |  | 1159.5062 | 203.9032
0 | 0 | 107.81 | 0 | 74351.902 | 955.045 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0027959 | 0.026952 | 0.029748 |  | 1159.4838 | 204.4388
0 | 0 | 1562.663 | 0 | 74459.712 | 954.334 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.040526 | 0.39067 | 0.43119 |  | 1159.454 | 205.12
0 | 0 | 431.749 | 0 | 76022.375 | 943.923 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.011197 | 0.10794 | 0.11913 |  | 1159.0228 | 215.0998
0 | 0 | 433.588 | 0 | 76454.124 | 941.857 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.011245 | 0.1084 | 0.11964 |  | 1158.9037 | 217.0467
0 | 0 | 123.695 | 0 | 76887.712 | 940.635 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0032079 | 0.030924 | 0.034132 |  | 1158.7841 | 218.1491
0 | 0 | 15.264 | 0 | 77011.407 | 940.369 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00039586 | 0.003816 | 0.0042119 |  | 1158.7499 | 218.3809
0 | 0 | 93.334 | 0 | 77026.671 | 940.362 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0024205 | 0.023334 | 0.025754 |  | 1158.7457 | 218.3837
0 | 0 | 71.346 | 0 | 77120.005 | 940.291 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0018503 | 0.017837 | 0.019687 |  | 1158.72 | 218.429
0 | 0 | 84.84 | 0 | 77191.351 | 940.217 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0022002 | 0.02121 | 0.02341 |  | 1158.7003 | 218.4833
0 | 0 | 900.987 | 0 | 77276.191 | 940.206 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.023366 | 0.22525 | 0.24861 |  | 1158.6769 | 218.4709
0 | 0 | 1143.471 | 0 | 78177.178 | 939.39 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.029655 | 0.28587 | 0.31552 |  | 1158.4283 | 219.0383
0 | 0 | 419.152 | 0 | 79320.649 | 929.221 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.01087 | 0.10479 | 0.11566 |  | 1158.1127 | 228.8917
0 | 0 | 513.182 | 0 | 79739.801 | 926.117 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013309 | 0.1283 | 0.1416 |  | 1157.9971 | 231.8801
0 | 0 | 9.217 | 0 | 80252.983 | 923.105 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00023903 | 0.0023042 | 0.0025433 |  | 1157.8555 | 234.7505
0 | 0 | 428.755 | 0 | 80262.2 | 923.053 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.011119 | 0.10719 | 0.11831 |  | 1157.8529 | 234.7999
0 | 0 | 17.801 | 0 | 80690.955 | 922.031 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00046165 | 0.0044503 | 0.0049119 |  | 1157.7346 | 235.7036
0 | 0 | 529.93 | 0 | 80708.756 | 921.915 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013743 | 0.13248 | 0.14623 |  | 1157.7297 | 235.8147
0 | 0 | 478.911 | 0 | 81238.686 | 918.699 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.01242 | 0.11973 | 0.13215 |  | 1157.5835 | 238.8845
0 | 0 | 100.857 | 0 | 81717.597 | 915.412 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0026156 | 0.025214 | 0.02783 |  | 1157.4513 | 242.0393
0 | Node 14 | 417.787 | 0 | 81818.454 | 915.801 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.010835 | 0.10445 | 0.11528 |  | 1157.4235 | 241.6225
Node 14 | Node 14 | 0 | Node 14 | 82236.241 | 920.33 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0 | 0 | 0 |  | 1157.3082 | 236.9782
Node 14 | 0 | 307.179 | Node 14 | 82236.241 | 920.33 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0079664 | 0.076795 | 0.084761 |  | 1157.3082 | 236.9782
0 | 0 | 762.598 | 0 | 82543.42 | 922.59 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.019777 | 0.19065 | 0.21043 |  | 1157.2235 | 234.6335
0 | 0 | 19.164 | 0 | 83306.018 | 931.409 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.000497 | 0.004791 | 0.005288 |  | 1157.013 | 225.604
0 | 0 | 148.277 | 0 | 83325.182 | 931.624 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0038454 | 0.037069 | 0.040915 |  | 1157.0078 | 225.3838
0 | 0 | 348.072 | 0 | 83473.459 | 932.08 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0090269 | 0.087018 | 0.096045 |  | 1156.9668 | 224.8868
0 | 0 | 476.185 | 0 | 83821.531 | 932.452 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.012349 | 0.11905 | 0.1314 |  | 1156.8708 | 224.4188
0 | 0 | 6.044 | 0 | 84297.716 | 929.365 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00015674 | 0.001511 | 0.0016677 |  | 1156.7394 | 227.3744
0 | 0 | 221.172 | 0 | 84303.76 | 929.327 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0057359 | 0.055293 | 0.061029 |  | 1156.7377 | 227.4107
0 | 0 | 166.015 | 0 | 84524.932 | 926.391 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0043054 | 0.041504 | 0.045809 |  | 1156.6767 | 230.2857
0 | 0 | 742.601 | 0 | 84690.947 | 927.174 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.019259 | 0.18565 | 0.20491 |  | 1156.6309 | 229.4569
0 | 0 | 941.334 | 0 | 85433.548 | 940.089 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.024412 | 0.23533 | 0.25975 |  | 1156.426 | 216.337
0 | 0 | 1017.084 | 0 | 86374.882 | 947.023 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.026377 | 0.25427 | 0.28065 |  | 1156.1662 | 209.1432
0 | 0 | 86.726 | 0 | 87391.966 | 956.232 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0022491 | 0.021681 | 0.023931 |  | 1155.8856 | 199.6536
0 | 0 | 556.545 | 0 | 87478.692 | 959.405 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.014433 | 0.13914 | 0.15357 |  | 1155.8617 | 196.4567
0 | 0 | 532.794 | 0 | 88035.237 | 960.418 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013817 | 0.1332 | 0.14702 |  | 1155.7081 | 195.2901
0 | 0 | 1142.263 | 0 | 88568.031 | 962.366 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.029623 | 0.28557 | 0.31519 |  | 1155.5611 | 193.1951
0 | 0 | 907.955 | 0 | 89710.294 | 967.934 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.023547 | 0.22699 | 0.25054 |  | 1155.2459 | 187.3119
0 | 0 | 291.556 | 0 | 90618.249 | 974.317 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0075612 | 0.072889 | 0.08045 |  | 1154.9954 | 180.6784
0 | 0 | 431.83 | 0 | 90909.805 | 976.244 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.011199 | 0.10796 | 0.11916 |  | 1154.9149 | 178.6709
0 | 0 | 126.171 | 0 | 91341.635 | 978.309 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0032721 | 0.031543 | 0.034815 |  | 1154.7957 | 176.4867
0 | 0 | 38.633 | 0 | 91467.806 | 978.6 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010019 | 0.0096583 | 0.01066 |  | 1154.7609 | 176.1609
0 | 0 | 588.887 | 0 | 91506.439 | 978.61 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.015272 | 0.14722 | 0.16249 |  | 1154.7503 | 176.1403
0 | 0 | 1134.058 | 0 | 92095.326 | 978.147 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.029411 | 0.28351 | 0.31293 |  | 1154.5878 | 176.4408
0 | 0 | 1288.94 | 0 | 93229.384 | 980.004 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.033427 | 0.32224 | 0.35566 |  | 1154.2749 | 174.2709
0 | 0 | 13.368 | 0 | 94518.324 | 985.238 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00034668 | 0.003342 | 0.0036887 |  | 1153.9192 | 168.6812
0 | 0 | 1425.987 | 0 | 94531.692 | 985.311 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.036981 | 0.3565 | 0.39348 |  | 1153.9155 | 168.6045
0 | 0 | 580.947 | 0 | 95957.679 | 994.899 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.015066 | 0.14524 | 0.1603 |  | 1153.522 | 158.623
0 | 0 | 109.277 | 0 | 96538.626 | 995.929 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.002834 | 0.027319 | 0.030153 |  | 1153.3617 | 157.4327
0 | 0 | 1167.273 | 0 | 96647.903 | 996.031 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.030272 | 0.29182 | 0.32209 |  | 1153.3316 | 157.3006
0 | 0 | 999.436 | 0 | 97815.176 | 995.77 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.025919 | 0.24986 | 0.27578 |  | 1153.0095 | 157.2395
0 | Node 8 | 90.387 | 0 | 98814.612 | 993.424 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0023441 | 0.022597 | 0.024941 |  | 1152.7337 | 159.3097
Node 8 | Node 8 | 0 | Node 8 | 98904.999 | 993.76 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0 | 0 | 0 |  | 1152.7088 | 158.9488
Node 8 | 0 | 68.279 | Node 8 | 98904.999 | 993.76 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0017707 | 0.01707 | 0.01884 |  | 1152.7088 | 158.9488
0 | 0 | 367.818 | 0 | 98973.278 | 993.671 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.009539 | 0.091954 | 0.10149 |  | 1152.6899 | 159.0189
0 | 0 | 16.492 | 0 | 99341.096 | 993.734 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0004277 | 0.004123 | 0.0045507 |  | 1152.5884 | 158.8544
0 | 0 | 24.024 | 0 | 99357.588 | 993.053 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00062304 | 0.006006 | 0.006629 |  | 1152.5839 | 159.5309
0 | 0 | 233.595 | 0 | 99381.612 | 993.719 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.006058 | 0.058399 | 0.064457 |  | 1152.5772 | 158.8582
0 | 0 | 65.122 | 0 | 99615.207 | 993.734 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0016889 | 0.016281 | 0.017969 |  | 1152.5128 | 158.7788
0 | 0 | 185.87 | 0 | 99680.329 | 993.06 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0048203 | 0.046467 | 0.051288 |  | 1152.4948 | 159.4348
0 | 0 | 60.604 | 0 | 99866.199 | 993.506 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0015717 | 0.015151 | 0.016723 |  | 1152.4435 | 158.9375
0 | 0 | 20.519 | 0 | 99926.803 | 994.7 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00053214 | 0.0051298 | 0.0056619 |  | 1152.4268 | 157.7268
0 | 0 | 2.275 | 0 | 99947.322 | 993.573 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 5.9e-05 | 0.00056875 | 0.00062775 |  | 1152.4211 | 158.8481
0 | 0 | 50.725 | 0 | 99949.597 | 994.208 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0013155 | 0.012681 | 0.013997 |  | 1152.4205 | 158.2125
0 | 0 | 237.072 | 0 | 100000.322 | 993.854 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0061482 | 0.059268 | 0.065416 |  | 1152.4065 | 158.5525
0 | 0 | 21.032 | 0 | 100237.394 | 995.8 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00054544 | 0.005258 | 0.0058034 |  | 1152.3411 | 156.5411
0 | 0 | 70.684 | 0 | 100258.426 | 997.358 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0018331 | 0.017671 | 0.019504 |  | 1152.3353 | 154.9773
0 | 0 | 27.078 | 0 | 100329.11 | 998.326 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00070224 | 0.0067695 | 0.0074717 |  | 1152.3158 | 153.9898
0 | 0 | 166.625 | 0 | 100356.188 | 996.918 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0043212 | 0.041656 | 0.045977 |  | 1152.3083 | 155.3903
0 | 0 | 4.079 | 0 | 100522.813 | 998.105 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00010578 | 0.0010197 | 0.0011255 |  | 1152.2623 | 154.1573
0 | 0 | 397.022 | 0 | 100526.892 | 998.106 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.010296 | 0.099255 | 0.10955 |  | 1152.2612 | 154.1552
0 | 0 | 31.081 | 0 | 100923.914 | 998.811 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00080605 | 0.0077703 | 0.0085763 |  | 1152.1517 | 153.3407
0 | 0 | 58 | 0 | 100954.995 | 999.402 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0015042 | 0.0145 | 0.016004 |  | 1152.1431 | 152.7411
0 | 0 | 725.071 | 0 | 101012.995 | 998.903 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.018804 | 0.18127 | 0.20007 |  | 1152.1271 | 153.2241
0 | 0 | 20.217 | 0 | 101738.066 | 1000.334 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00052431 | 0.0050543 | 0.0055786 |  | 1151.927 | 151.593
0 | 0 | 55.37 | 0 | 101758.283 | 1000.993 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.001436 | 0.013842 | 0.015278 |  | 1151.9214 | 150.9284
0 | 0 | 56.387 | 0 | 101813.653 | 1000.472 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0014623 | 0.014097 | 0.015559 |  | 1151.9062 | 151.4342
0 | 0 | 342.885 | 0 | 101870.04 | 1001.704 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0088923 | 0.085721 | 0.094614 |  | 1151.8906 | 150.1866
0 | 0 | 156.302 | 0 | 102212.925 | 1004.389 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0040535 | 0.039075 | 0.043129 |  | 1151.796 | 147.407
0 | 0 | 112.735 | 0 | 102369.227 | 1006.483 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0029237 | 0.028184 | 0.031107 |  | 1151.7529 | 145.2699
0 | 0 | 15.512 | 0 | 102481.962 | 1006.577 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00040229 | 0.003878 | 0.0042803 |  | 1151.7218 | 145.1448
0 | 0 | 202.632 | 0 | 102497.474 | 1007.431 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.005255 | 0.050658 | 0.055913 |  | 1151.7175 | 144.2865
0 | 0 | 56.696 | 0 | 102700.106 | 1009.628 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0014703 | 0.014174 | 0.015644 |  | 1151.6616 | 142.0336
0 | 0 | 152.504 | 0 | 102756.802 | 1009.272 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.003955 | 0.038126 | 0.042081 |  | 1151.6459 | 142.3739
0 | 0 | 21.261 | 0 | 102909.306 | 1011.756 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00055138 | 0.0053152 | 0.0058666 |  | 1151.6038 | 139.8478
0 | 0 | 27.008 | 0 | 102930.567 | 1011.16 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00070042 | 0.006752 | 0.0074524 |  | 1151.598 | 140.438
0 | Node 15 | 199.933 | 0 | 102957.575 | 1012.521 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.005185 | 0.049983 | 0.055168 |  | 1151.5905 | 139.0695
Node 15 | Node 15 | 0 | Node 15 | 103157.508 | 1014.216 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0 | 0 | 0 |  | 1151.5353 | 137.3193
Node 15 | 0 | 62.239 | Node 15 | 103157.508 | 1014.216 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0016141 | 0.01556 | 0.017174 |  | 1151.5353 | 137.3193
0 | 0 | 43.266 | 0 | 103219.747 | 1013.47 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0011221 | 0.010817 | 0.011939 |  | 1151.5182 | 138.0482
0 | 0 | 58.511 | 0 | 103263.013 | 1014.988 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0015174 | 0.014628 | 0.016145 |  | 1151.5062 | 136.5182
0 | 0 | 70.335 | 0 | 103321.524 | 1012.681 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0018241 | 0.017584 | 0.019408 |  | 1151.4901 | 138.8091
0 | 0 | 27.347 | 0 | 103391.859 | 1014.679 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00070921 | 0.0068367 | 0.007546 |  | 1151.4707 | 136.7917
0 | 0 | 30.99 | 0 | 103419.206 | 1014.522 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00080369 | 0.0077475 | 0.0085512 |  | 1151.4631 | 136.9411
0 | 0 | 45.829 | 0 | 103450.196 | 1013.201 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0011885 | 0.011457 | 0.012646 |  | 1151.4546 | 138.2536
0 | 0 | 529.703 | 0 | 103496.025 | 1013.949 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013737 | 0.13243 | 0.14616 |  | 1151.4419 | 137.4929
0 | 0 | 566.085 | 0 | 104025.728 | 1007.872 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.014681 | 0.14152 | 0.1562 |  | 1151.2958 | 143.4238
0 | Node 16 | 896.938 | 0 | 104591.813 | 999.772 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.023261 | 0.22423 | 0.2475 |  | 1151.1396 | 151.3676
Node 16 | Node 16 | 0 | Node 16 | 105488.751 | 990.794 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0 | 0 | 0 |  | 1150.8921 | 160.0981
Node 16 | 0 | 674.373 | Node 16 | 105488.751 | 990.794 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.017489 | 0.16859 | 0.18608 |  | 1150.8921 | 160.0981
0 | 0 | 283.186 | 0 | 106163.124 | 999.431 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0073441 | 0.070796 | 0.078141 |  | 1150.706 | 151.275
0 | 0 | 322.863 | 0 | 106446.31 | 1000.769 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0083731 | 0.080716 | 0.089089 |  | 1150.6279 | 149.8589
0 | 0 | 105.294 | 0 | 106769.173 | 1000.552 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0027307 | 0.026323 | 0.029054 |  | 1150.5388 | 149.9868
0 | 0 | 157.387 | 0 | 106874.467 | 1001.573 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0040817 | 0.039347 | 0.043428 |  | 1150.5097 | 148.9367
0 | 0 | 172.013 | 0 | 107031.854 | 1004.523 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.004461 | 0.043003 | 0.047464 |  | 1150.4663 | 145.9433
0 | 0 | 509.84 | 0 | 107203.867 | 1008.886 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.013222 | 0.12746 | 0.14068 |  | 1150.4188 | 141.5328
0 | 0 | 259.924 | 0 | 107713.707 | 1018.318 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0067408 | 0.064981 | 0.071722 |  | 1150.2781 | 131.9601
0 | 0 | 273.06 | 0 | 107973.631 | 1020.473 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0070815 | 0.068265 | 0.075347 |  | 1150.2064 | 129.7334
0 | 0 | 193.977 | 0 | 108246.691 | 1024.205 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0050306 | 0.048494 | 0.053525 |  | 1150.1311 | 125.9261
0 | 0 | 206.916 | 0 | 108440.668 | 1028.097 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0053661 | 0.051729 | 0.057095 |  | 1150.0775 | 121.9805
0 | 0 | 297.136 | 0 | 108647.584 | 1031.926 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0077059 | 0.074284 | 0.08199 |  | 1150.0204 | 118.0944
0 | 0 | 37.001 | 0 | 108944.72 | 1029.743 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00095958 | 0.0092503 | 0.01021 |  | 1149.9385 | 120.1955
0 | 0 | 68.43 | 0 | 108981.721 | 1029.9009 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0017747 | 0.017108 | 0.018882 |  | 1149.9282 | 120.0273
0 | 0 | 117.343 | 0 | 109050.151 | 1030.193 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0030432 | 0.029336 | 0.032379 |  | 1149.9094 | 119.7163
0 | 0 | 9.614 | 0 | 109167.494 | 1030.6939 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00024933 | 0.0024035 | 0.0026528 |  | 1149.877 | 119.1831
0 | 0 | 2.937 | 0 | 109177.108 | 1030.7349 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 7.6168e-05 | 0.00073425 | 0.00081042 |  | 1149.8743 | 119.1394
0 | 0 | 115.529 | 0 | 109180.045 | 1030.7475 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0029961 | 0.028882 | 0.031878 |  | 1149.8735 | 119.1261
0 | 0 | 52.263 | 0 | 109295.574 | 1031.2406 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0013554 | 0.013066 | 0.014421 |  | 1149.8416 | 118.601
0 | 0 | 6.662 | 0 | 109347.837 | 1031.4637 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00017277 | 0.0016655 | 0.0018383 |  | 1149.8272 | 118.3635
0 | 0 | 19.877 | 0 | 109354.499 | 1031.4921 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00051549 | 0.0049692 | 0.0054847 |  | 1149.8254 | 118.3333
0 | 0 | 28.71 | 0 | 109374.376 | 1031.577 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00074456 | 0.0071775 | 0.0079221 |  | 1149.8199 | 118.2429
0 | 0 | 8.97 | 0 | 109403.086 | 1031.6995 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00023263 | 0.0022425 | 0.0024751 |  | 1149.812 | 118.1125
0 | 0 | 33.883 | 0 | 109412.056 | 1031.7378 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00087872 | 0.0084708 | 0.0093495 |  | 1149.8095 | 118.0717
0 | 0 | 13.277 | 0 | 109445.939 | 1031.8824 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00034432 | 0.0033193 | 0.0036636 |  | 1149.8002 | 117.9177
0 | 0 | 20.095 | 0 | 109459.216 | 1031.9391 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00052114 | 0.0050238 | 0.0055449 |  | 1149.7965 | 117.8574
0 | 0 | 55.568 | 0 | 109479.311 | 1032.0249 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0014411 | 0.013892 | 0.015333 |  | 1149.7909 | 117.7661
0 | 0 | 3.226 | 0 | 109534.879 | 1032.2621 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 8.3663e-05 | 0.0008065 | 0.00089016 |  | 1149.7756 | 117.5136
0 | 0 | 35.701 | 0 | 109538.105 | 1032.2758 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00092587 | 0.0089253 | 0.0098511 |  | 1149.7747 | 117.4989
0 | 0 | 18.225 | 0 | 109573.806 | 1032.4282 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00047265 | 0.0045563 | 0.0050289 |  | 1149.7649 | 117.3367
0 | 0 | 47.567 | 0 | 109592.031 | 1032.506 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0012336 | 0.011892 | 0.013125 |  | 1149.7598 | 117.2538
0 | 0 | 27.236 | 0 | 109639.598 | 1032.709 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00070634 | 0.006809 | 0.0075153 |  | 1149.7467 | 117.0377
0 | 0 | 49.652 | 0 | 109666.834 | 1032.8253 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0012877 | 0.012413 | 0.013701 |  | 1149.7392 | 116.9139
0 | 0 | 15.065 | 0 | 109716.486 | 1033.0372 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00039069 | 0.0037663 | 0.0041569 |  | 1149.7255 | 116.6883
0 | 0 | 2.993 | 0 | 109731.551 | 1033.1015 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 7.762e-05 | 0.00074825 | 0.00082587 |  | 1149.7213 | 116.6198
0 | 0 | 20.478 | 0 | 109734.544 | 1033.1143 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00053107 | 0.0051195 | 0.0056506 |  | 1149.7205 | 116.6062
0 | 0 | 55.746 | 0 | 109755.022 | 1033.2017 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0014457 | 0.013936 | 0.015382 |  | 1149.7149 | 116.5131
0 | 0 | 23.002 | 0 | 109810.768 | 1033.4397 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00059653 | 0.0057505 | 0.006347 |  | 1149.6995 | 116.2598
0 | 0 | 6.857 | 0 | 109833.77 | 1033.5379 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00017783 | 0.0017143 | 0.0018921 |  | 1149.6931 | 116.1553
0 | 0 | 6.836 | 0 | 109840.627 | 1033.5671 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00017728 | 0.001709 | 0.0018863 |  | 1149.6912 | 116.1241
0 | 0 | 46.564 | 0 | 109847.463 | 1033.5963 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0012076 | 0.011641 | 0.012849 |  | 1149.6894 | 116.0931
0 | 0 | 32.456 | 0 | 109894.027 | 1033.7951 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00084171 | 0.008114 | 0.0089557 |  | 1149.6765 | 115.8815
0 | 0 | 9.599 | 0 | 109926.483 | 1033.9336 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00024894 | 0.0023998 | 0.0026487 |  | 1149.6676 | 115.734
0 | 0 | 21.324 | 0 | 109936.082 | 1033.9746 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00055301 | 0.005331 | 0.005884 |  | 1149.6649 | 115.6903
0 | 0 | 6.95 | 0 | 109957.406 | 1034.0656 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00018024 | 0.0017375 | 0.0019177 |  | 1149.659 | 115.5934
0 | 0 | 10.173 | 0 | 109964.356 | 1034.0952 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00026383 | 0.0025432 | 0.0028071 |  | 1149.6571 | 115.5619
0 | 0 | 33.913 | 0 | 109974.529 | 1034.1387 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0008795 | 0.0084783 | 0.0093577 |  | 1149.6543 | 115.5156
0 | 0 | 14.465 | 0 | 110008.442 | 1034.2834 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00037513 | 0.0036162 | 0.0039914 |  | 1149.6449 | 115.3615
0 | 0 | 12.948 | 0 | 110022.907 | 1034.3452 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00033579 | 0.003237 | 0.0035728 |  | 1149.6409 | 115.2958
0 | 0 | 28.337 | 0 | 110035.855 | 1034.4004 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00073489 | 0.0070842 | 0.0078191 |  | 1149.6374 | 115.2369
0 | 0 | 16.46 | 0 | 110064.192 | 1034.5214 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00042687 | 0.004115 | 0.0045419 |  | 1149.6296 | 115.1082
0 | 0 | 39.601 | 0 | 110080.652 | 1034.5917 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.001027 | 0.0099002 | 0.010927 |  | 1149.625 | 115.0334
0 | 0 | 23.521 | 0 | 110120.253 | 1034.7607 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00060999 | 0.0058802 | 0.0064902 |  | 1149.6141 | 114.8534
0 | 0 | 69.244 | 0 | 110143.774 | 1034.8611 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0017958 | 0.017311 | 0.019107 |  | 1149.6076 | 114.7465
0 | 0 | 41.317 | 0 | 110213.018 | 1035.1566 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010715 | 0.010329 | 0.011401 |  | 1149.5885 | 114.4318
0 | 0 | 42.204 | 0 | 110254.335 | 1035.333 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010945 | 0.010551 | 0.011646 |  | 1149.5771 | 114.2441
0 | 0 | 60.705 | 0 | 110296.539 | 1035.5132 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0015743 | 0.015176 | 0.016751 |  | 1149.5654 | 114.0523
0 | 0 | 1.12 | 0 | 110357.244 | 1035.7723 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 2.9046e-05 | 0.00028 | 0.00030905 |  | 1149.5487 | 113.7764
0 | 0 | 8.772 | 0 | 110358.364 | 1035.777 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00022749 | 0.002193 | 0.0024205 |  | 1149.5484 | 113.7713
0 | 0 | 38.936 | 0 | 110367.136 | 1035.8145 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010098 | 0.009734 | 0.010744 |  | 1149.546 | 113.7315
0 | 0 | 2.004 | 0 | 110406.072 | 1035.9807 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 5.1972e-05 | 0.000501 | 0.00055297 |  | 1149.5352 | 113.5545
0 | 0 | 50.247 | 0 | 110408.076 | 1035.9892 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0013031 | 0.012562 | 0.013865 |  | 1149.5347 | 113.5454
0 | 0 | 24.124 | 0 | 110458.323 | 1036.2037 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00062563 | 0.006031 | 0.0066566 |  | 1149.5208 | 113.3171
0 | 0 | 55.653 | 0 | 110482.447 | 1036.3067 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0014433 | 0.013913 | 0.015357 |  | 1149.5141 | 113.2075
0 | 0 | 19.249 | 0 | 110538.1 | 1036.5442 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0004992 | 0.0048123 | 0.0053115 |  | 1149.4988 | 112.9546
0 | 0 | 74.248 | 0 | 110557.349 | 1036.6264 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0019255 | 0.018562 | 0.020488 |  | 1149.4935 | 112.8671
0 | 0 | 13.53 | 0 | 110631.597 | 1036.9433 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00035089 | 0.0033825 | 0.0037334 |  | 1149.473 | 112.5297
0 | 0 | 15.674 | 0 | 110645.127 | 1037.0011 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00040649 | 0.0039185 | 0.004325 |  | 1149.4693 | 112.4682
0 | 0 | 42.39 | 0 | 110660.801 | 1037.068 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010993 | 0.010597 | 0.011697 |  | 1149.4649 | 112.397
0 | 0 | 45.858 | 0 | 110703.191 | 1037.2489 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0011893 | 0.011464 | 0.012654 |  | 1149.4532 | 112.2043
0 | 0 | 11.362 | 0 | 110749.049 | 1037.4447 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00029466 | 0.0028405 | 0.0031352 |  | 1149.4406 | 111.9959
0 | 0 | 37.484 | 0 | 110760.411 | 1037.4932 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00097211 | 0.009371 | 0.010343 |  | 1149.4374 | 111.9443
0 | 0 | 29.473 | 0 | 110797.895 | 1037.6532 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00076435 | 0.0073682 | 0.0081326 |  | 1149.4271 | 111.7739
0 | 0 | 2.451 | 0 | 110827.368 | 1037.779 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 6.3564e-05 | 0.00061275 | 0.00067631 |  | 1149.419 | 111.64
0 | 0 | 50 | 0 | 110829.819 | 1037.7894 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0012967 | 0.0125 | 0.013797 |  | 1149.4183 | 111.6289
0 | 0 | 88.299 | 0 | 110879.819 | 1038.0028 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0022899 | 0.022075 | 0.024365 |  | 1149.4045 | 111.4017
0 | 0 | 20.335 | 0 | 110968.118 | 1038.3797 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00052737 | 0.0050838 | 0.0056111 |  | 1149.3801 | 111.0004
0 | 0 | 26.857 | 0 | 110988.453 | 1038.4665 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00069651 | 0.0067142 | 0.0074108 |  | 1149.3745 | 110.908
0 | 0 | 11.75 | 0 | 111015.31 | 1038.5812 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00030472 | 0.0029375 | 0.0032422 |  | 1149.3671 | 110.7859
0 | 0 | 8.842 | 0 | 111027.06 | 1038.6313 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00022931 | 0.0022105 | 0.0024398 |  | 1149.3639 | 110.7325
0 | 0 | 23.831 | 0 | 111035.902 | 1038.6691 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00061803 | 0.0059578 | 0.0065758 |  | 1149.3614 | 110.6924
0 | 0 | 37.019 | 0 | 111059.733 | 1038.7708 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00096005 | 0.0092548 | 0.010215 |  | 1149.3549 | 110.5841
0 | 0 | 12.503 | 0 | 111096.752 | 1038.9288 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00032425 | 0.0031257 | 0.00345 |  | 1149.3446 | 110.4158
0 | 0 | 17.77 | 0 | 111109.255 | 1038.9822 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00046085 | 0.0044425 | 0.0049033 |  | 1149.3412 | 110.359
0 | 0 | 41.785 | 0 | 111127.025 | 1039.058 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0010836 | 0.010446 | 0.01153 |  | 1149.3363 | 110.2783
0 | 0 | 3.519 | 0 | 111168.81 | 1039.2364 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 9.1261e-05 | 0.00087975 | 0.00097101 |  | 1149.3248 | 110.0884
0 | 0 | 16.872 | 0 | 111172.329 | 1039.2514 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00043756 | 0.004218 | 0.0046556 |  | 1149.3238 | 110.0724
0 | 0 | 33.743 | 0 | 111189.201 | 1039.3234 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00087509 | 0.0084358 | 0.0093108 |  | 1149.3191 | 109.9957
0 | 0 | 17.142 | 0 | 111222.944 | 1039.4674 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00044456 | 0.0042855 | 0.0047301 |  | 1149.3098 | 109.8424
0 | 0 | 31.399 | 0 | 111240.086 | 1039.5406 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.0008143 | 0.0078498 | 0.008664 |  | 1149.3051 | 109.7645
0 | 0 | 13.941 | 0 | 111271.485 | 1039.6746 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00036154 | 0.0034853 | 0.0038468 |  | 1149.2964 | 109.6218
0 | 0 | 5.143 | 0 | 111285.426 | 1039.7341 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00013338 | 0.0012857 | 0.0014191 |  | 1149.2926 | 109.5584
0 | 0 | 29.59 | 0 | 111290.569 | 1039.7561 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00076738 | 0.0073975 | 0.0081649 |  | 1149.2912 | 109.5351
0 | Node 20 | 27.55 | 0 | 111320.159 | 1039.8824 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0.00071448 | 0.0068875 | 0.007602 |  | 1149.283 | 109.4006
|  |  | Node 20 | 111347.709 | 1044 |  | 2200 | 2200 | 2200 | 1.2491 | 0.3286 | 0.0001 | 0.010367 | 0 | 0 | 0 |  | 1149.2754 | 105.2754
Note on J2: User: From Base Data Sheet

## Pump main
| PROJECT: | Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
| OPTION: | Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
| BASE YEAR: | 2008
| RATES: | April 2008
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
| DESCRIPTION |  |  | UNIT/RATE | P1 | P2 | P3 | P4 | P5 | P6 | TOTAL
| Start Chainage |  |  |  | 0 | 0 | 0
| End Chainage |  |  |  | 61368 | 0 | 0
PUMP HEAD AND FLOW RATE
| Flow rate (duty) (Qd) 347 day average flow |  |  | m³/s | 1.2491 | 1.2491 | 1.2491 | 0 | 0 | 0
| installed capacity (Qi = Qp x (1 + Ps)) |  |  | m³/s | 1.7812 | 1.7812 | 1.7812 | 0 | 0 | 0
| Required peak capacity (Qp = Q365 x Peak Refill factor) |  |  | m³/s | 1.425 | 1.425 | 1.425 | 0 | 0 | 0
|  | Peak factor | 1.2
Head pumped (under normal operating conditions):
| static head (Hst) |  |  | m | 117.58 | 0 | 0 | 0 | 0 | 0 | 117.58
| rising main friction loss(Hf) |  |  | m | 112.9759 | 0 | 0 | 0 | 0 | 0 | 112.9759
| rising main secondary losses(Hv) |  |  | m | 15.342 | 0 | 0 | 0 | 0 | 0 | 15.342
| pump station secondary losses(Hps) |  |  | m | 4 | 0 | 0 | 0 | 0 | 0 | 4
| Additional pumping head |  |  | m | -46
| Total head (duty) (Hd = Hst + Hf + Hv + Hps) |  |  | m | 203.8979 | 0 | 0 | 0 | 0 | 0 | 203.8979
Head pumped (under peak operating conditions):
| static head (Hst) |  |  | m | 117.58 | 0 | 0 | 0 | 0 | 0 | 117.58
| rising main friction loss(Hf) |  |  | m | 145.7837 | 0 | 0 | 0 | 0 | 0 | 145.7837
| rising main secondary losses(Hv) |  |  | m | 15.342 | 0 | 0 | 0 | 0 | 0 | 15.342
| pump station secondary losses(Hps) |  |  | m | 4 | 0 | 0 | 0 | 0 | 0 | 4
| Additional pumping head |  |  | m | -52
| Total head (peak) (Hd = Hst + Hf + Hv + Hps) |  |  | m | 230.7057 | 0 | 0 | 0 | 0 | 0 | 230.7057
All further information on this sheet is calculated for normal operating conditions
RISING MAIN
| length (L) |  |  | m | 61368 | 0 | 0 | 0 | 0 | 0 | 61368
| outside diameter (OD) |  |  | mm | 1000 | 1000 | 1000 | 0 | 0 | 0
| inner diameter (ID) |  |  | mm | 984 | 972 | 972 | 0 | 0 | 0
| minimum yield stress of steel |  |  | MPa | 290 | 290 | 290 | 0 | 0 | 0
| minimum wall thickness (tmin = D/160) |  |  | mm | 6 | 6 | 6 | 0 | 0 | 0
| required wall thickness (t) |  |  | mm | 8 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
| chosen wall thickness (t) |  |  | mm | 8 | 14 | 14 | 0 | 0 | 0
| number of pipes in parallel (n) |  |  | no | 1 | 1 | 1 | 1 | 1 | 1
| flow per pipe (Qp) |  |  | m³/s | 1.2491 | 1.2491 | 1.2491 | 0 | 0 | 0
| velocity per pipe (Vp) |  |  | m/s | 1.6425 | 1.6833 | 1.6833 | 0 | 0 | 0
| secondary losses in rising main |  |  | m/km | 0.25 | 0.25 | 0.25 | 0 | 0 | 0
INPUT FOR COLEBROOK-WHITE & DARCY-WEISBACH
| friction coefficient (l) |  |  | - | 0.013174 | 0.013183 | 0.013183 | #DIV/0! | #DIV/0! | #DIV/0!
| effective roughness (k) |  |  | mm | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Reynolds number (Re) |  |  | - | 1430320.45 | 1447978.7272 | 1447978.7272 | 0 | 0 | 0
| pipe cross sectional area (A) |  |  | m² | 0.76047 | 0.74203 | 0.74203 | 0 | 0 | 0
| kinematic viscosity (nu) |  |  | m²/s | 1.13e-06 | 1.13e-06 | 1.13e-06 | 1.13e-06 | 1.13e-06 | 1.13e-06
| gravity constant (g) |  |  | m/s² | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81
PUMP SET EFFICIENCIES
| Efficiency of pump (Ep) |  |  | % | 90% | 90% | 90% | 90% | 90% | 90%
| Efficiency of motor (Em) |  |  | % | 97% | 97% | 97% | 97% | 97% | 97%
| Average loss in efficiency between major overhauls (Eo) |  |  | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
| Overall efficiency (Et = Ep x Em x (1 - Eo)) |  |  | % | 85.99% | 85.99% | 85.99% | 85.99% | 85.99% | 85.99%
| MW/MVA ratio (power factor Pf) |  |  | - | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
| Standby allowance (Ps) |  |  | % | 25% | 25% | 25% | 25% | 25% | 25%
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
| DESCRIPTION |  |  | UNIT/RATE | P1 | P2 | P3 | P4 | P5 | P6 | TOTAL
PUMP STATION POWER REQUIREMENTS
| power req'd at duty point (Pd = 9.81 x 1000 x Qd x Hd / Et) |  |  | MW | 2.9055 | 0 | 0 | 0 | 0 | 0 | 2.9055
| power absorbed at Qd: (Pd / Pf) |  |  | MVA | 3.0266 | 0 | 0 | 0 | 0 | 0 | 3.0266
| power absorbed at Qi: (Pd x Pf x (1 + Ps)) |  |  | MVA | 3.7833 | 0 | 0 | 0 | 0 | 0 | 3.7833
| head pumped (Hd) |  |  | m | 203.8979 | 0 | 0 | 0 | 0 | 0 | 203.8979
| Energy consumed over 24 hours (continuous use) |  | 24 | MWh | 69.7331 | 0 | 0 | 0 | 0 | 0 | 69.7331
Paramater used for pump stations costing | power req'd at peak point (Pp = 9.81 x 1000 x Qp x Hp / Et) |  |  | MW | 3.7505 | 0 | 0 | 0 | 0 | 0 | 3.7505
ADDITIONAL PUMP STATION PARAMETERS
| Access road to pump station |  |  | km | 1 | 0 | 0 | 0 | 0 | 0 | 1 | BREAKDOWN OF COSTS FOR USE IN TABLE 2:
0 Included in Weir Cost | Hours of storage in forebay (Ts) |  |  | h | 0 | 0 | 0 | 0 | 0 | 0
| Forebay volume (Vf = Qd x Ts) |  |  | m³ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COST OF ELEC/ | COST OF PUMP/ | COST OF CIVIL | TRANSMISSION | TOTAL
| PUMP STATION COST (single stage vertical) | [10 empty] | MECH EQUIPMENT | MOTOR ONLY | CONSTRUCTION | LINE COST | (CHECK)
| mechanical: pump & motor |  | 60% | of total A1 | 12770782.2044 | 0 | 0 | 0 | 0 | 0 | 12770782.2044 |  | 12770782.2044
| mechanical: valves |  | 25% | of total A1 | 5321159.2518 | 0 | 0 | 0 | 0 | 0 | 5321159.2518 | 5321159.2518
| mechanical: pipework |  | 15% | of total A1 | 3192695.5511 | 0 | 0 | 0 | 0 | 0 | 3192695.5511 | 3192695.5511
| Total mechanical cost (total A1) |  | 50% | of total A2 | 21284637.0073 | 0 | 0 | 0 | 0 | 0 | 21284637.0073
| Total electrical cost |  | 20% | of total A2 | 8513854.8029 | 0 | 0 | 0 | 0 | 0 | 8513854.8029 | 8513854.8029
| Total civil cost |  | 30% | of total A2 | 12770782.2044 | 0 | 0 | 0 | 0 | 0 | 12770782.2044 |  |  | 12770782.2044
| Subtotal: elec/mech/civil cost (total A2) |  |  |  | 42569274.0147 | 0 | 0 | 0 | 0 | 0 | 42569274.0147
| access road cost |  | R/km | 3000000 | 3000000 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 0 | 3000000
| forebay |  | R/m3 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Subtotal: (total A3) |  |  |  | 45569274.0147 | 0 | 0 | 0 | 0 | 0 | 45569274.0147 | 17027709.6059 | 12770782.2044 | 15770782.2044 |  | 45569274.0147
| landscaping |  |  | 5% | 2278463.7007 | 0 | 0 | 0 | 0 | 0 | 2278463.7007 | 0 | 0 | 2278463.7007
| miscellaneous |  |  | 10% | 4556927.4015 | 0 | 0 | 0 | 0 | 0 | 4556927.4015 | 0 | 0 | 4556927.4015
| Subtotal: (total A) |  |  |  | 52404665.1169 | 0 | 0 | 0 | 0 | 0 | 52404665.1169 | 17027709.6059 | 12770782.2044 | 22606173.3066 |  | 52404665.1169
| Preliminary and General |  |  | 30% | 15721399.5351 | 0 | 0 | 0 | 0 | 0 | 15721399.5351 | 5108312.8818 | 3831234.6613 | 6781851.992
| Preliminary Work |  |  |  | 455692.7401 | 0 | 0 | 0 | 0 | 0 | 455692.7401 | 0 | 0 | 455692.7401
| Subtotal: (total B) |  |  |  | 68581757.3921 | 0 | 0 | 0 | 0 | 0 | 68581757.3921 | 22136022.4876 | 16602016.8657 | 29843718.0387 |  | 68581757.3921
| Contingencies |  |  | 20% | 13716351.4784 | 0 | 0 | 0 | 0 | 0 | 13716351.4784 | 4427204.4975 | 3320403.3731 | 5968743.6077
| Subtotal: (total C) |  |  |  | 82298108.8705 | 0 | 0 | 0 | 0 | 0 | 82298108.8705 | 26563226.9852 | 19922420.2389 | 35812461.6465 |  | 82298108.8705
| Planning, design and supervision fees |  |  | 15% | 12344716.3306 | 0 | 0 | 0 | 0 | 0 | 12344716.3306 | 3984484.0478 | 2988363.0358 | 5371869.247
| Total cost excluding VAT (total D) |  |  |  | 94642825.2011 | 0 | 0 | 0 | 0 | 0 | 94642825.2011 | 30547711.0329 | 22910783.2747 | 41184330.8935 |  | 94642825.2011
| Cost of ESKOM transmission lines to site |  |  |  | 22300000 | 0 | 0 | 0 | 0 | 0 | 22300000 | 0 | 0 | 0 | 22300000 | 22300000
| Connection fee |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value Added Tax |  |  | 14% | 16371995.5282 | 0 | 0 | 0 | 0 | 0 | 16371995.5282 | 4276679.5446 | 3207509.6585 | 5765806.3251 | 3122000 | 16371995.5282
| Relocations and land acquisition |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
| Total cost including VAT |  |  |  | 133314820.7293 | 0 | 0 | 0 | 0 | 0 | 133314820.7293 | 34824390.5776 | 26118292.9332 | 46950137.2186 | 25422000 | 133314820.7293
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
ANNUAL COST OF ELECTRICITY (24 h operation)
| Network Access Charge |  |  |  | 305082.47 | 0 | 0 | 0 | 0 | 0 | 305082.47
| Network Demand Charge |  |  |  | 178678.1898 | 0 | 0 | 0 | 0 | 0 | 178678.1898
| Reactive Energy Charge |  |  |  | 128375.5131 | 0 | 0 | 0 | 0 | 0 | 128375.5131
| Voltage Surcharge |  |  |  | 514584.5277 | 0 | 0 | 0 | 0 | 0 | 514584.5277
| Annual energy Cost (R/MWh) |  |  | 173.336 | 4194280.5012 | 0 | 0 | 0 | 0 | 0 | 4194280.5012
| Service & Admin Charge |  |  |  | 48055.9 | 0 | 0 | 0 | 0 | 0 | 48055.9
| Total annual cost |  |  |  | 5369057.1019 | 0 | 0 | 0 | 0 | 0 | 5369057.1019
PUMP STATION, RISING MAIN AND ELECTRICITY COST CALCULATIONS
| DESCRIPTION |  |  | UNIT/RATE | P1 | P2 | P3 | P4 | P5 | P6 | TOTAL
RISING MAIN COST
| Pipeline |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Road, river and rail crossings
| (a) national & provincial road |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| (b) national & provincial road |  |  |  | #REF! | #REF! | #REF!
| (c) river |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| (d) rail |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total A |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| landscaping |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| miscellaneous |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total B |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| preliminary and general |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| preliminary works |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| accomodation |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total C |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| contingencies |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total D |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| planning, design and supervision |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Sub-total E |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| VAT |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Relocations and land acquisition |  |  |  | #REF! | #REF! |  |  |  |  | #REF!
| Total cost including VAT |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[5 empty] | 130 | 70 | 70
Note on B63: User: Power required at duty
Note on B64: User: Power absorbed at duty
Note on B65: User: Power absorbed at installed
Note on B68: User: Power required at peak operating
Note on F10: njordaan: Total length of pipeline from Mokolo Weir to Steenbokpan.
Note on F17: njordaan: Static head from long section between weir site and highest point. Weir site = 820.04m Highest point = 937.62m
Note on F21: njordaan: Total head required at pump station at weir to pump water all the way to Steenbokpan and ensure a pressure of 15m at Steenbokpan = 203.9m at normal conditions, i.e. 2% losses and allowing for 5% downtime for normal maintanence (Value from Node Results or Vertical Allignment plot with hydraulic gradient, Civil Designer). Therefore chose this value to give the value of "Total head" = 203.9m.
Note on F28: njordaan: Total head required at pump station at weir to pump water all the way to Steenbokpan and ensure a pressure of 15m at Steenbokpan = 230.4m at peak flow conditions, i.e. 2% losses x 1.2 peak factor (Value from Node Results or Vertical Allignment plot with hydraulic gradient, Civil Designer). Therefore chose this value to give the value of "Total head" = 230.4m.

## Pump model
| PROJECT: |  | Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
| OPTION: |  | Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
| BASE YEAR: |  | 2008
| RATES: |  | April 2008
| Number of pumps |  |  |  | 4 | (excluding standby) |  | Down Time | 18 | days
| Standby pumps |  |  |  | 1 |  |  | Down Time Peak | 1.2
| Flow per pump 347 days |  |  |  | 0.31227 | m³/s |  | Refill period | 90 | days
| Total flow 347 days |  |  |  | 1.2491 | m³/s |  | Refill Peak | 1.2
| Total flow 365 days |  |  |  | 1.1875 | m³/s | [6 empty] | Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
| Pumps Active |  |  |  | 347 | days per annum |  | 49.4356 | weeks |  |  |  | Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
| Pumping Peak factor based on refill period |  |  |  | 1.2 | [7 empty] | DEMAND PROJECTIONS AND REQUIRED PUMPING RATE & TIME
ELECTRICITY COSTS
| YEAR | HOURS | NUMBER OF PUMPS |  | MWh | DEMAND & | ANNUAL ELECTRICITY COST FOR PUMP STATIONS | [5 empty] | YEAR | NET DEMAND | LOSSES % | GROSS DEMAND | PUMP RATE 347 days | MAX YIELD | PUMP RATE | HOURS
|  | PUMPED | INSTALLED | ACTIVE | per day | ACCESS | ENERGY | SERVICE | REACTIVE & SURCHARGE | TOTAL | TOTAL ESCALATED | ESCALATION FACTOR (Real) |  | million m3/yr |  | million m3/yr | m3/s | m3/s | m3/s | h
| 2008 | [8 empty] | 0 | 0 | 1 | 2008 | 0 | 0% | 0 | 0 | 0 | 0 | 0
| 2009 | [8 empty] | 0 | 0 | 1.2 | 2009 | 0 | 0% | 0 | 0 | 0 | 0 | 0
0 | 2010 | [8 empty] | 0 | 0 | 1.44 | 2010 | 0 | 0% | 0 | 0 | 0 | 0 | 0
1 | 2011 | 17.6586 | 5 | 3 | 38.481 | 362820.4949 | 2314536.7582 | 48055.9 | 506994.2231 | 3232407.3762 | 5585599.946 | 1.728 | 2011 | 20.2522 | 2% | 20.6655 | 0.68929 | 0 | 0.68929 | 13.244
2 | 2012 | 18.3273 | 5 | 4 | 53.2507 | 483760.6598 | 3202903.3377 | 48055.9 | 521330.7532 | 4256050.6507 | 8825346.6294 | 2.0736 | 2012 | 28.0254 | 2% | 28.5974 | 0.95386 | 0 | 0.95386 | 18.3273
3 | 2013 | 24 | 5 | 4 | 69.7331 | 483760.6598 | 4194280.5012 | 48055.9 | 642960.0409 | 5369057.1019 | 13359932.1678 | 2.4883 | 2013 | 36.7 | 2% | 37.449 | 1.2491 | 0 | 1.2491 | 24
4 | 2014 | 24 | 5 | 4 | 69.7331 | 483760.6598 | 4194280.5012 | 48055.9 | 642960.0409 | 5369057.1019 | 13359932.1678 | 2.4883 | 2014 | 36.7 | 2% | 37.449 | 1.2491 | 0 | 1.2491 | 24
5 | 2015 | 23.891 | 5 | 3 | 52.0623 | 362820.4949 | 3131424.6794 | 48055.9 | 640623.1447 | 4182924.219 | 10408453.9926 | 2.4883 | 2015 | 27.4 | 2% | 27.9592 | 0.93257 | 0 | 0.93257 | 17.9183
6 | 2016 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2016 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
7 | 2017 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2017 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
8 | 2018 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2018 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
9 | 2019 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2019 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
10 | 2020 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2020 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
11 | 2021 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2021 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
12 | 2022 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2022 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
13 | 2023 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2023 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
14 | 2024 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2024 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
15 | 2025 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2025 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
16 | 2026 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2026 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
17 | 2027 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2027 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
18 | 2028 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2028 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
19 | 2029 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2029 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
20 | 2030 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2030 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
21 | 2031 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2031 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
22 | 2032 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2032 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
23 | 2033 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2033 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
24 | 2034 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2034 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
25 | 2035 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2035 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
26 | 2036 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2036 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
27 | 2037 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2037 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
28 | 2038 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2038 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
29 | 2039 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2039 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
30 | 2040 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2040 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
31 | 2041 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2041 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
32 | 2042 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2042 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
33 | 2043 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2043 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
34 | 2044 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2044 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
35 | 2045 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2045 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
36 | 2046 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2046 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
37 | 2047 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2047 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
38 | 2048 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2048 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
39 | 2049 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2049 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
40 | 2050 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2050 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
41 | 2051 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2051 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
42 | 2052 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2052 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
43 | 2053 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2053 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
44 | 2054 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2054 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
45 | 2055 | 18.7684 | 5 | 4 | 54.5325 | 483760.6598 | 3279995.9233 | 48055.9 | 530789.0266 | 4342601.5098 | 10805782.1888 | 2.4883 | 2055 | 28.7 | 2% | 29.2857 | 0.97682 | 0 | 0.97682 | 18.7684
| TOTAL |  |  |  |  | 21527349.3623 | 148237262.7103 | 2162515.5 | 24186429.2683 | 196113556.8408 | 483770552.4559

## BOQ Rising main 1000
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008
RATES: |  | April 2008
RISING MAIN - 1000mm DIAMETER PIPELINE COST CALCULATIONS | [6 empty] | P1 | P1 | P2 | P2 | P3 | P3 | P4 | P4 | P5 | P5 | P6 | P6
No | Pay Ref | Description |  |  | Unit | Rate | Quantity | Amount | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | Quantity | Amount
Rands
[7 empty] | 1 |  | 1 |  | 1
1. |  | Route Clearing & grubbing
|  | (a) Sparse, bush & trees |  |  | Ha | 10300 | 76 | 782800 | 0 | 0 | 0 | 0 | [6 empty] | 76 | 782800
2. |  | Road, river and rail crossings |  |  | 1000
|  | (a) national & provincial road |  |  | no | 1330000 | 2 | 2660000 | 0 | 0 | 0 | 0 | [6 empty] | 2 | 2660000 | CALCULATIONS FOR D/t
|  | (b) gravel road |  |  | no | 260000 | 2 | 520000 | 0 | 0 | 0 | 0 | [6 empty] | 2 | 520000 | highest static pressure in pipeline | m | 230.4
|  | (c) river |  |  | no | 720000 | 3 | 2160000 | 0 | 0 | 0 | 0 | [6 empty] | 3 | 2160000 | outside diameter (OD) | mm | 1000
|  | (d) rail |  |  | no | 1330000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | minimum yield stress of steel | MPa | 290
[21 empty] | minimum wall thickness (tmin = D/160) | mm | 6
3. |  | Trench Excvation & backfill | [18 empty] | required wall thickness (t) | mm | 8
|  | (a) Excavation | [18 empty] | chosen wall thickness (t) | mm | 8
|  | All materials |  |  | m³ | 50 | 156166.6364 | 7808331.8219 | 0 | 0 | 0 | 0 | [6 empty] | 156166.6364 | 7808331.8219
|  | E/O Hard |  |  | m³ | 100 | 62466.6546 | 6246665.4576 | 0 | 0 | 0 | 0 | [6 empty] | 62466.6546 | 6246665.4576 | D/t |  | 130
(b) Bedding
|  | From trench |  |  | m³ | 135 | 4607.4874 | 622010.7936 | 0 | 0 | 0 | 0 | [6 empty] | 4607.4874 | 622010.7936
|  | From commercial sources |  |  | m³ | 235 | 10750.8038 | 2526438.9024 | 0 | 0 | 0 | 0 | [6 empty] | 10750.8038 | 2526438.9024
(c) Bedding Cradle & Fill Blanket
|  | From trench |  |  | m³ | 210 | 15367.8781 | 3227254.392 | 0 | 0 | 0 | 0 | [6 empty] | 15367.8781 | 3227254.392
|  | From commercial sources |  |  | m³ | 245 | 35858.3821 | 8785303.6227 | 0 | 0 | 0 | 0 | [6 empty] | 35858.3821 | 8785303.6227
(d) Main Fill
|  | From trench |  |  | m³ | 55 | 68994.3575 | 3794689.6619 | 0 | 0 | 0 | 0 | [6 empty] | 68994.3575 | 3794689.6619
|  | (e) Spoil |  |  | m³ | 45 | 67196.9135 | 3023861.109 | 0 | 0 | 0 | 0 | [6 empty] | 67196.9135 | 3023861.109
4. |  | Pipelines
(a) Supply of steel pipe: D/t ratio as specified. Sintakote external coating and epoxy internal lining
|  | Dia (mm) | Grade | D/t
| P1 | 1000 | API Grade X42 | 130 | m | 3969 | 25394 | 100788786 | [10 empty] | 25394 | 100788786 |  |  | 1000130API Grade X42
[9 empty] | 0 | 0 | [8 empty] | 0 | 0
[11 empty] | 0 | 0 | [6 empty] | 0 | 0 | 43403
|  | (b) Laying & jointing (% of a) |  |  |  | 20% |  | 20157757.2 |  | 0 |  | 0 | [7 empty] | 20157757.2
|  | (c) Air valve, Isolating Valve, Scour Valve, Access | [18 empty] | Length section 18,4,5,6,7 = | 25394 | m
|  | All valve types, incl chamber - civil & mechanical components |  |  | m | 290 | 25394 | 7364260 | 0 | 0 | 0 | 0 | [6 empty] | 25394 | 7364260 | Cathodic Protection section 1-7 = | 27273028
[21 empty] | Length section 1-7 = | 41949 | m
|  | (d) Cathodic Protection |  |  | m | 16509839.8778 | 1 |  | 0 | 0 | 0 | 0 | [7 empty] | 9659490.677
|  | Other 1 | [16 empty] | 0 | 0
|  | Other 2 | [16 empty] | 0 | 0
|  | Other 3 | [16 empty] | 0 | 0
|  | SUB-TOTAL A | [5 empty] | 170468158.9611 |  | 0 |  | 0 | [7 empty] | 180127649.6382
5. |  | Landscaping & EIA Remediation (% of Sub-total A) |  |  | % | 5 |  | 8523407.9481 |  | 0 |  | 0 | [7 empty] | 9006382.4819
6. |  | Miscellaneous (% of Sub-total A) |  |  | % | 10 |  | 17046815.8961 |  | 0 |  | 0 | [7 empty] | 18012764.9638
|  | SUB TOTAL B | [5 empty] | 196038382.8053 |  | 0 |  | 0 | [7 empty] | 207146797.0839
7. |  | Preliminary & General (% of Sub-total B) |  |  | % | 30 |  | 58811514.8416 |  | 0 |  | 0 | [7 empty] | 62144039.1252
To include below
8. |  | Preliminary works
|  | (a) Access road |  |  | km | 350000 | 25.394 | 8887900 | 0 | 0 | 0 | 0 | [6 empty] | 25.394 | 8887900
|  | (b) Electricity to site |  |  | Sum | [14 empty] | 0
|  | (c) Water to site - construction |  |  | Sum | [14 empty] | 0
(not potable)
|  | (d) Railhead & materials handling |  |  | Sum | [14 empty] | 0
9. |  | Accommodation |  |  | Sum | [14 empty] | 0
|  | SUB TOTAL C | [5 empty] | 263737797.6469 |  | 0 |  | 0 | [7 empty] | 278178736.2091
9. |  | Contingencies
|  | (% of Sub-total C) |  |  | % | 20 |  | 52747559.5294 |  | 0 |  | 0 | [7 empty] | 55635747.2418
|  | SUB TOTAL D | [5 empty] | 316485357.1762 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 333814483.4509
10. |  | Planning design & supervision
|  | (% of Sub-total D) |  |  | % | 15 |  | 47472803.5764 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 50072172.5176
|  | SUB TOTAL E | [5 empty] | 363958160.7527 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 383886655.9685
11. |  | VAT (% of sub total E) |  |  | % | 14 |  | 50954142.5054 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 53744131.8356
|  | NETT PROJECT COST | [5 empty] | 414912303.2581 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 437630787.8041
12. |  | Cost of relocations |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
13. |  | Cost of land acquisition |  |  | Sum |  |  | 4016258.6196 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 4016258.6196 | 10000000 | = Social costs from Russell Aird for entire Phase 1B (from River Bend Weir)
[21 empty] | 63228 | = Total length of pipe for option 1B
|  | TOTAL RISING MAIN COST | [5 empty] | 418928561.8777 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 441647046.4237
|  | TOTAL RISING MAIN COST (EXCL VAT, RELOC, LAND ACQ) | [5 empty] | 320501615.7958 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 383886655.9685
Note on D73: User: Include in P&G percentage
Note on X47: njordaan: Length of 1000mm dia pipeline for Mokolo Dam option (pipe sections 1-7) for which the cost of cathodic protection was given by Neil Webb.
Note on Y52: njordaan: Value from spreadsheets received from Neil Webb.
Note on Z20: njordaan: Waarde van druk benodig by weir om hoogte + wrywingverliese te oorkom. Waarde van Node results en vertical allignment se hydroliese gradient (Civ Des)

## BOQ Rising main 900
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008
RATES: |  | April 2008
GRAVITY MAIN - 900mm DIAMETER PIPELINE COST CALCULATIONS | [6 empty] | P1 | P1 | P2 | P2 | P3 | P3 | P4 | P4 | P5 | P5 | P6 | P6
No | Pay Ref | Description |  |  | Unit | Rate | Quantity | Amount | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | Quantity | Amount
Rands
[7 empty] | 1 |  | 1 |  | 1
1. |  | Route Clearing & grubbing
|  | (a) Sparse, bush & trees |  |  | Ha | 10300 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
2. |  | Road, river and rail crossings |  |  | 900
|  | (a) national & provincial road |  |  | no | 1270000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | CALCULATIONS FOR D/t
|  | (b) gravel road |  |  | no | 220000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | highest static pressure in pipeline | m | 0
|  | (c) river |  |  | no | 670000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | outside diameter (OD) | mm | 900
|  | (d) rail |  |  | no | 1270000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | minimum yield stress of steel | MPa | 290
[21 empty] | minimum wall thickness (tmin = D/160) | mm | 6
3. |  | Trench Excvation & backfill | [18 empty] | required wall thickness (t) | mm | 0
|  | (a) Excavation | [18 empty] | chosen wall thickness (t) | mm | 6
|  | All materials |  |  | m³ | 50 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | E/O Hard |  |  | m³ | 100 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | D/t |  | 150
(b) Bedding
|  | From trench |  |  | m³ | 135 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | From commercial sources |  |  | m³ | 235 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
(c) Bedding Cradle & Fill Blanket
|  | From trench |  |  | m³ | 210 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | From commercial sources |  |  | m³ | 245 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
(d) Main Fill
|  | From trench |  |  | m³ | 55 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (e) Spoil |  |  | m³ | 45 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
4. |  | Pipelines
(a) Supply of steel pipe: D/t ratio as specified. Sintakote external coating and epoxy internal lining
|  | Dia (mm) | Grade | D/t
| P1 | 1000 | API Grade X42 | 150 | m | 3625 | 0 | 0 | [10 empty] | 0 | 0 |  |  | 1000150API Grade X42
[9 empty] | 0 | 0 | [8 empty] | 0 | 0
[11 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | (b) Laying & jointing (% of a) |  |  |  | 20% |  | 0 |  | 0 |  | 0 | [7 empty] | 0
(c) Air valve, Isolating Valve, Scour Valve, Access
|  | All valve types, incl chamber - civil & mechanical components |  |  | m | 290 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (d) Cathodic Protection |  |  | m | 390 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | Other 1 | [16 empty] | 0 | 0
|  | Other 2 | [16 empty] | 0 | 0
|  | Other 3 | [16 empty] | 0 | 0
|  | SUB-TOTAL A | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
5. |  | Landscaping & EIA Remediation (% of Sub-total A) |  |  | % | 5 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
6. |  | Miscellaneous (% of Sub-total A) |  |  | % | 10 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
|  | SUB TOTAL B | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
7. |  | Preliminary & General (% of Sub-total B) |  |  | % | 30 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
To include below
8. |  | Preliminary works
|  | (a) Access road |  |  | km | 350000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (b) Electricity to site |  |  | Sum | [14 empty] | 0
|  | (c) Water to site - construction |  |  | Sum | [14 empty] | 0
(not potable)
|  | (d) Railhead & materials handling |  |  | Sum | [14 empty] | 0
9. |  | Accommodation |  |  | Sum | [14 empty] | 0
|  | SUB TOTAL C | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
9. |  | Contingencies
|  | (% of Sub-total C) |  |  | % | 20 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
|  | SUB TOTAL D | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
10. |  | Planning design & supervision
|  | (% of Sub-total D) |  |  | % | 15 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | SUB TOTAL E | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
11. |  | VAT (% of sub total E) |  |  | % | 14 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | NETT PROJECT COST | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12. |  | Cost of relocations |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
13. |  | Cost of land acquisition |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL RISING MAIN COST | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL RISING MAIN COST (EXCL VAT,FEES) | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Note on D73: User: Include in P&G percentage

## BOQ Rising main 800
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008
RATES: |  | April 2008
RISING MAIN - 800mm DIAMETER PIPELINE COST CALCULATIONS | [6 empty] | P1 | P1 | P2 | P2 | P3 | P3 | P4 | P4 | P5 | P5 | P6 | P6
No | Pay Ref | Description |  |  | Unit | Rate | Quantity | Amount | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | Quantity | Amount
Rands
[7 empty] | 1 |  | 1 |  | 1
1. |  | Route Clearing & grubbing
|  | (a) Sparse, bush & trees |  |  | Ha | 10300 | 114 | 1174200 | 0 | 0 | 0 | 0 | [6 empty] | 114 | 1174200
2. |  | Road, river and rail crossings |  |  | 800
|  | (a) national & provincial road |  |  | no | 1230000 | 5 | 6150000 | 0 | 0 | 0 | 0 | [6 empty] | 5 | 6150000 | CALCULATIONS FOR D/t
|  | (b) gravel road |  |  | no | 200000 | 7 | 1400000 | 0 | 0 | 0 | 0 | [6 empty] | 7 | 1400000 | highest static pressure in pipeline | m | 129.8
|  | (c) river |  |  | no | 620000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | outside diameter (OD) | mm | 800
|  | (d) rail |  |  | no | 1230000 | 2 | 2460000 | 0 | 0 | 0 | 0 | [6 empty] | 2 | 2460000 | minimum yield stress of steel | MPa | 290
[21 empty] | minimum wall thickness (tmin = D/160) | mm | 5
3. |  | Trench Excvation & backfill | [18 empty] | required wall thickness (t) | mm | 4
|  | (a) Excavation | [18 empty] | chosen wall thickness (t) | mm | 5
|  | All materials |  |  | m³ | 50 | 232669.4701 | 11633473.5036 | 0 | 0 | 0 | 0 | [6 empty] | 232669.4701 | 11633473.5036
|  | E/O Hard |  |  | m³ | 100 | 93067.788 | 9306778.8029 | 0 | 0 | 0 | 0 | [6 empty] | 93067.788 | 9306778.8029 | D/t |  | 160
(b) Bedding
|  | From trench |  |  | m³ | 135 | 6864.601 | 926721.1296 | 0 | 0 | 0 | 0 | [6 empty] | 6864.601 | 926721.1296
|  | From commercial sources |  |  | m³ | 235 | 16017.4022 | 3764089.5264 | 0 | 0 | 0 | 0 | [6 empty] | 16017.4022 | 3764089.5264
(c) Bedding Cradle & Fill Blanket
|  | From trench |  |  | m³ | 210 | 22896.2865 | 4808220.157 | 0 | 0 | 0 | 0 | [6 empty] | 22896.2865 | 4808220.157
|  | From commercial sources |  |  | m³ | 245 | 53424.6684 | 13089043.7608 | 0 | 0 | 0 | 0 | [6 empty] | 53424.6684 | 13089043.7608
(d) Main Fill
|  | From trench |  |  | m³ | 55 | 102793.2788 | 5653630.3327 | 0 | 0 | 0 | 0 | [6 empty] | 102793.2788 | 5653630.3327
|  | (e) Spoil |  |  | m³ | 45 | 100115.3039 | 4505188.6743 | 0 | 0 | 0 | 0 | [6 empty] | 100115.3039 | 4505188.6743
4. |  | Pipelines
(a) Supply of steel pipe: D/t ratio as specified. Sintakote external coating and epoxy internal lining
|  | Dia (mm) | Grade | D/t
| P1 | 1000 | API Grade X42 | 160 | m | 3488 | 37834 | 131964992 | [10 empty] | 37834 | 131964992 |  |  | 1000160API Grade X42
[9 empty] | 0 | 0 | [8 empty] | 0 | 0
[11 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | (b) Laying & jointing (% of a) |  |  |  | 20% |  | 26392998.4 |  | 0 |  | 0 | [7 empty] | 26392998.4
(c) Air valve, Isolating Valve, Scour Valve, Access
|  | All valve types, incl chamber - civil & mechanical components |  |  | m | 290 | 37834 | 10971860 | 0 | 0 | 0 | 0 | [6 empty] | 37834 | 10971860
|  | (d) Cathodic Protection |  |  | m | 18163708 | 1 |  | 0 | 0 | 0 | 0 | [7 empty] | 18163708
|  | Other 1 | [16 empty] | 0 | 0
|  | Other 2 | [16 empty] | 0 | 0
|  | Other 3 | [16 empty] | 0 | 0
|  | SUB-TOTAL A | [5 empty] | 234201196.2875 |  | 0 |  | 0 | [7 empty] | 252364904.2875
5. |  | Landscaping & EIA Remediation (% of Sub-total A) |  |  | % | 5 |  | 11710059.8144 |  | 0 |  | 0 | [7 empty] | 12618245.2144
6. |  | Miscellaneous (% of Sub-total A) |  |  | % | 10 |  | 23420119.6287 |  | 0 |  | 0 | [7 empty] | 25236490.4287
|  | SUB TOTAL B | [5 empty] | 269331375.7306 |  | 0 |  | 0 | [7 empty] | 290219639.9306
7. |  | Preliminary & General (% of Sub-total B) |  |  | % | 30 |  | 80799412.7192 |  | 0 |  | 0 | [7 empty] | 87065891.9792
To include below
8. |  | Preliminary works
|  | (a) Access road |  |  | km | 350000 | 37.834 | 13241900 | 0 | 0 | 0 | 0 | [6 empty] | 37.834 | 13241900
|  | (b) Electricity to site |  |  | Sum | [14 empty] | 0
|  | (c) Water to site - construction |  |  | Sum | [14 empty] | 0
(not potable)
|  | (d) Railhead & materials handling |  |  | Sum | [14 empty] | 0
9. |  | Accommodation |  |  | Sum | [14 empty] | 0
|  | SUB TOTAL C | [5 empty] | 363372688.4498 |  | 0 |  | 0 | [7 empty] | 390527431.9098
9. |  | Contingencies
|  | (% of Sub-total C) |  |  | % | 20 |  | 72674537.69 |  | 0 |  | 0 | [7 empty] | 78105486.382
|  | SUB TOTAL D | [5 empty] | 436047226.1397 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 468632918.2917
10. |  | Planning design & supervision
|  | (% of Sub-total D) |  |  | % | 15 |  | 65407083.921 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 70294937.7438
|  | SUB TOTAL E | [5 empty] | 501454310.0607 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 538927856.0355
11. |  | VAT (% of sub total E) |  |  | % | 14 |  | 70203603.4085 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 75449899.845
|  | NETT PROJECT COST | [5 empty] | 571657913.4692 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 614377755.8804
12. |  | Cost of relocations |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
13. |  | Cost of land acquisition |  |  | Sum |  |  | 5983741.3804 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 5983741.3804 | 10000000 | = Social costs from Russell Aird for entire Phase 1B (from River Bend Weir)
[21 empty] | 63228 | = Total length of pipe for option 1B
|  | TOTAL RISING MAIN COST | [5 empty] | 577641654.8496 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 620361497.2608
|  | TOTAL RISING MAIN COST (EXCL VAT, RELOC, LAND ACQ) | [5 empty] | 442030967.5201 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 538927856.0355
Note on D73: User: Include in P&G percentage
Note on H54: njordaan: Value from spreadsheets received from Neil Webb.
Note on Z20: njordaan: Highest pressure at nodes along this section of pipeline.

## BOQ Rising main 700
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008
RATES: |  | April 2008
GRAVITY MAIN - 700mm DIAMETER PIPELINE COST CALCULATIONS | [6 empty] | P1 | P1 | P2 | P2 | P3 | P3 | P4 | P4 | P5 | P5 | P6 | P6
No | Pay Ref | Description |  |  | Unit | Rate | Quantity | Amount | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | Quantity | Amount
Rands
[7 empty] | 1 |  | 1 |  | 1
1. |  | Route Clearing & grubbing
|  | (a) Sparse, bush & trees |  |  | Ha | 10300 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
2. |  | Road, river and rail crossings |  |  | 700
|  | (a) national & provincial road |  |  | no | 1200000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | CALCULATIONS FOR D/t
|  | (b) gravel road |  |  | no | 170000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | highest static pressure in pipeline | m | 0
|  | (c) river |  |  | no | 580000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | outside diameter (OD) | mm | 700
|  | (d) rail |  |  | no | 1200000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | minimum yield stress of steel | MPa | 290
[21 empty] | minimum wall thickness (tmin = D/160) | mm | 4
3. |  | Trench Excvation & backfill | [18 empty] | required wall thickness (t) | mm | 0
|  | (a) Excavation | [18 empty] | chosen wall thickness (t) | mm | 4
|  | All materials |  |  | m³ | 50 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | E/O Hard |  |  | m³ | 100 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | D/t |  | 180
(b) Bedding
|  | From trench |  |  | m³ | 135 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | From commercial sources |  |  | m³ | 235 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
(c) Bedding Cradle & Fill Blanket
|  | From trench |  |  | m³ | 210 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | From commercial sources |  |  | m³ | 245 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
(d) Main Fill
|  | From trench |  |  | m³ | 55 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (e) Spoil |  |  | m³ | 45 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
4. |  | Pipelines
(a) Supply of steel pipe: D/t ratio as specified. Sintakote external coating and epoxy internal lining
|  | Dia (mm) | Grade | D/t
| P1 | 1000 | API Grade X42 | 130 | m | 3969 | 0 | 0 | [10 empty] | 0 | 0 |  |  | 1000130API Grade X42
[9 empty] | 0 | 0 | [8 empty] | 0 | 0
[11 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | (b) Laying & jointing (% of a) |  |  |  | 20% |  | 0 |  | 0 |  | 0 | [7 empty] | 0
(c) Air valve, Isolating Valve, Scour Valve, Access
|  | All valve types, incl chamber - civil & mechanical components |  |  | m | 290 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (d) Cathodic Protection |  |  | m | 390 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | Other 1 | [16 empty] | 0 | 0
|  | Other 2 | [16 empty] | 0 | 0
|  | Other 3 | [16 empty] | 0 | 0
|  | SUB-TOTAL A | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
5. |  | Landscaping & EIA Remediation (% of Sub-total A) |  |  | % | 5 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
6. |  | Miscellaneous (% of Sub-total A) |  |  | % | 10 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
|  | SUB TOTAL B | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
7. |  | Preliminary & General (% of Sub-total B) |  |  | % | 30 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
To include below
8. |  | Preliminary works
|  | (a) Access road |  |  | km | 350000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (b) Electricity to site |  |  | Sum | [14 empty] | 0
|  | (c) Water to site - construction |  |  | Sum | [14 empty] | 0
(not potable)
|  | (d) Railhead & materials handling |  |  | Sum | [14 empty] | 0
9. |  | Accommodation |  |  | Sum | [14 empty] | 0
|  | SUB TOTAL C | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
9. |  | Contingencies
|  | (% of Sub-total C) |  |  | % | 20 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
|  | SUB TOTAL D | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
10. |  | Planning design & supervision
|  | (% of Sub-total D) |  |  | % | 15 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | SUB TOTAL E | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
11. |  | VAT (% of sub total E) |  |  | % | 14 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | NETT PROJECT COST | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12. |  | Cost of relocations |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
13. |  | Cost of land acquisition |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL RISING MAIN COST | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL RISING MAIN COST (EXCL VAT) | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Note on D73: User: Include in P&G percentage

## BOQ Rising main 500
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008
RATES: |  | April 2008
GRAVITY MAIN - 500mm DIAMETER PIPELINE COST CALCULATIONS | [6 empty] | P1 | P1 | P2 | P2 | P3 | P3 | P4 | P4 | P5 | P5 | P6 | P6
No | Pay Ref | Description |  |  | Unit | Rate | Quantity | Amount | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | Quantity | Amount
Rands
[7 empty] | 1 |  | 1 |  | 1
1. |  | Route Clearing & grubbing
|  | (a) Sparse, bush & trees |  |  | Ha | 10300 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
2. |  | Road, river and rail crossings |  |  | 500
|  | (a) national & provincial road |  |  | no | 1130000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | CALCULATIONS FOR D/t
|  | (b) gravel road |  |  | no | 130000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | highest static pressure in pipeline | m | 0
|  | (c) river |  |  | no | 510000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | outside diameter (OD) | mm | 500
|  | (d) rail |  |  | no | 1130000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | minimum yield stress of steel | MPa | 290
[21 empty] | minimum wall thickness (tmin = D/160) | mm | 3
3. |  | Trench Excvation & backfill | [18 empty] | required wall thickness (t) | mm | 0
|  | (a) Excavation | [18 empty] | chosen wall thickness (t) | mm | 3
|  | All materials |  |  | m³ | 50 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | E/O Hard |  |  | m³ | 100 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | D/t |  | 170
(b) Bedding
|  | From trench |  |  | m³ | 135 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | From commercial sources |  |  | m³ | 235 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
(c) Bedding Cradle & Fill Blanket
|  | From trench |  |  | m³ | 210 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | From commercial sources |  |  | m³ | 245 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
(d) Main Fill
|  | From trench |  |  | m³ | 55 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (e) Spoil |  |  | m³ | 45 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
4. |  | Pipelines
(a) Supply of steel pipe: D/t ratio as specified. Sintakote external coating and epoxy internal lining
|  | Dia (mm) | Grade | D/t
| P1 | 1000 | API Grade X42 | 130 | m | 3969 | 0 | 0 | [10 empty] | 0 | 0 |  |  | 1000130API Grade X42
[9 empty] | 0 | 0 | [8 empty] | 0 | 0
[11 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | (b) Laying & jointing (% of a) |  |  |  | 20% |  | 0 |  | 0 |  | 0 | [7 empty] | 0
(c) Air valve, Isolating Valve, Scour Valve, Access
|  | All valve types, incl chamber - civil & mechanical components |  |  | m | 290 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (d) Cathodic Protection |  |  | m | 390 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | Other 1 | [16 empty] | 0 | 0
|  | Other 2 | [16 empty] | 0 | 0
|  | Other 3 | [16 empty] | 0 | 0
|  | SUB-TOTAL A | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
5. |  | Landscaping & EIA Remediation (% of Sub-total A) |  |  | % | 5 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
6. |  | Miscellaneous (% of Sub-total A) |  |  | % | 10 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
|  | SUB TOTAL B | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
7. |  | Preliminary & General (% of Sub-total B) |  |  | % | 30 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
To include below
8. |  | Preliminary works
|  | (a) Access road |  |  | km | 350000 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0
|  | (b) Electricity to site |  |  | Sum | [14 empty] | 0
|  | (c) Water to site - construction |  |  | Sum | [14 empty] | 0
(not potable)
|  | (d) Railhead & materials handling |  |  | Sum | [14 empty] | 0
9. |  | Accommodation |  |  | Sum | [14 empty] | 0
|  | SUB TOTAL C | [5 empty] | 0 |  | 0 |  | 0 | [7 empty] | 0
9. |  | Contingencies
|  | (% of Sub-total C) |  |  | % | 20 |  | 0 |  | 0 |  | 0 | [7 empty] | 0
|  | SUB TOTAL D | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
10. |  | Planning design & supervision
|  | (% of Sub-total D) |  |  | % | 15 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | SUB TOTAL E | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
11. |  | VAT (% of sub total E) |  |  | % | 14 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | NETT PROJECT COST | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12. |  | Cost of relocations |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
13. |  | Cost of land acquisition |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL RISING MAIN COST | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL RISING MAIN COST (EXCL VAT) | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Note on D73: User: Include in P&G percentage

## BOQ Pump St
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
| BASE YEAR: |  | 2008
| RATES: |  | April 2008
| PUMP STATION COST CALCULATIONS |  |  |  |  | P1 | P1 | P2 | P2 | P3 | P3 | P4 | P4 | P5 | P5 | P6 | P6
| No | PAY | DESCRIPTION | UNIT | RATE | Quantity | Amount | Quantity | Amount | Quantity | Amount | QUANTITY | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT | Quantity | Amount
|  | REF |  |  | 2008
RAND
| 1. |  | Mechanical and Electrical | Sum |  |  | 29798491.8103 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 29798491.8103 | 0.65392 | 53458494.3077
| 2. |  | Civils
|  |  | (a) (% of 1) | % | 42.86% |  | 12770782.2044 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 12770782.2044 | 0.28025 | 22910783.2747
|  |  | (c) Permanent access road | km | 3000000 | 1 | 3000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000000 | 0.065834 | 5382000
|  |  | (d) Forebay ( 1 hour storage) | m3 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SUB-TOTAL A |  |  |  | 45569274.0147 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 45569274.0147
| 3. | 11.0 | Landscaping (% of Sub-total A) | % | 5 |  | 2278463.7007 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2278463.7007
| 4. | 12.0 | Miscellaneous (% of Sub-total A) | % | 10 |  | 4556927.4015 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 4556927.4015
|  |  | SUB TOTAL B |  |  |  | 52404665.1169 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 52404665.1169
| 5. | 13.0 | Preliminary & General (% of sub-total B) | % | 30 |  | 15721399.5351 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 15721399.5351
| 6. | 14.0 | Preliminary works
REMOVE |  | 14.1 | (a) Access road | km |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
|  | 14.2 | (b) Electricity to site | Sum |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
|  | 14.3 | (c) Water to site - construction | Sum |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
(not potable)
|  | 14.4 | (d) Infrastructure for materials handling | % | 1 |  | 455692.7401 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 455692.7401
(% of Sub-total A)
| 7. | 15.0 | Accommodation | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  | SUB TOTAL C |  |  |  | 68126064.652 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 68126064.652
| 7. | 17.0 | Contingencies
|  |  | (% of sub total C) | % | 20 |  | 13625212.9304 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 13625212.9304
|  |  | SUB TOTAL D |  |  |  | 81751277.5824 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 81751277.5824
| 8. | 16.0 | Planning design & supervision fees,
time cost & transport
|  |  | (% of sub total D) | % | 15 |  | 12262691.6374 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 12262691.6374
|  |  | SUB TOTAL E |  |  |  | 94013969.2197 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 94013969.2197
| 9. | 18.0 | VAT (% of sub total E) | % | 14 |  | 13161955.6908 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 13161955.6908
|  |  | NETT PUMP STATION COST |  |  |  | 107175924.9105 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 107175924.9105
| 10. | 19.0 | Cost of relocations | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| 11. | 20.0 | Cost of land acquisition | Sum |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| 12. | 21.0 | Cost of ESKOM transmission lines to site + Connection fee | Sum |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  | TOTAL PUMP STATION COST |  |  |  | 107175924.9105 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 107175924.9105
|  |  | TOTAL PUMP STATION COST (EXCL VAT) |  |  |  | 81751277.5824 |  | 0 |  | 0 |  | 0 |  | 0 |  | #REF! |  | 94013969.2197
Note on D31: User: Include in P&G percentage

## BOQ Weir
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008
RATES: |  | April 2008
MOKOLO ABSTRACTION WEIR COST MODEL |  |  | ABSTRACTION WEIR COST MODEL | [6 empty] | ABSTRACTION WEIR COST MODEL | [6 empty] | ABSTRACTION WEIR COST MODEL
|  |  | Mokolo Weir | [6 empty] | Mokolo De-Silting Works | [6 empty] | Mokolo Balancing Dam
No | DESCRIPTION | AMOUNT | No | PAY | DESCRIPTION | UNIT | RATE | QUANTITY | AMOUNT | No | PAY | DESCRIPTION | UNIT | RATE | QUANTITY | AMOUNT | No | PAY | DESCRIPTION | UNIT | RATE | QUANTITY | AMOUNT
|  |  |  | REF |  |  | 2008-04-01 |  |  |  | REF |  |  | 2008-04-01 |  |  |  | REF |  |  | 2008-04-01
|  | (Rand) |  |  |  |  | (Rand) |  | (Rand) |  |  |  |  | (Rand) |  | (Rand) |  |  |  |  | (Rand) |  | (Rand)
1 | Mokolo Works |  | 1 | 1 | Clearing |  |  |  |  | 1 | 1 | Clearing |  |  |  |  | 1 | 1 | Clearing
| a) Abstraction Weir | 159011916.9654 |  | 1.1 | a) Sparse | ha | 5500 | 0 | 0 |  | 1.1 | a) Sparse | ha | 5500 | 0 | 0 |  | 1.1 | a) Sparse | ha | 5500 | 0 | 0
| b) Siltation Works | 14686932.2059 |  | 1.2 | b) Bush | ha | 16490 | 1 | 16490 |  | 1.2 | b) Bush | ha | 16490 | 1 | 16490 |  | 1.2 | b) Bush | ha | 16490 | 1 | 16490
| c) Balancing Dam | 18467014.6865 |  | 1.3 | c) Trees | ha | 27480 | 1 | 27480 |  | 1.3 | c) Trees | ha | 27480 | 1 | 27480 |  | 1.3 | c) Trees | ha | 27480 | 3 | 82440
| SUB-TOTAL BOSCHKOP | 192165863.8578 | 2 | 2 | River diversion | Sum |  |  |  | 2 | 2 | Excavation |  |  |  |  | 2 | 2 | Excavation
[11 empty] | 2.1 | (a) Bulk | [5 empty] | 2.1 | (a) Bulk
| SUB-TOTAL CIVIL (EXCL VAT) | 137857623.7969 | 3 | 3 | Excavation | [5 empty] | 2.1.1 | (i) all materials | m3 | 40 | 3048 | 121920 |  | 2.1.1 | (i) all materials | m3 | 40 | 40000 | 1600000
|  |  |  | 3.1 | (a) Bulk | [5 empty] | 2.1.2 | (ii) extra over for rock | m3 | 80 | 1828.8 | 146304 |  | 2.1.2 | (ii) extra over for rock | m3 | 80 | 24000 | 1920000
|  |  |  | 3.1.1 | (i) all materials | m3 | 40 | 13513 | 540520
| SUB-TOTAL MECHANICAL (EXCL VAT) | 35356870.5344 |  | 3.1.2 | (ii) extra over for rock | m3 | 80 | 1351.3 | 108104 |  | 2.2 | (b) Confined | [5 empty] | 2.2 | (b) Confined
[11 empty] | 2.2.1 | (i) all materials | m3 | 60 | 0 | 0 |  | 2.2.1 | (i) all materials | m3 | 60 | 6000 | 360000
|  |  |  | 3.2 | (b) Confined | [5 empty] | 2.2.2 | (ii) extra over for rock | m3 | 100 | 0 | 0 |  | 2.2.2 | (ii) extra over for rock | m3 | 100 | 3600 | 360000
|  |  |  | 3.2.1 | (i) all materials | m3 | 60 | 0 | 0
|  |  |  | 3.2.2 | (ii) extra over for rock | m3 | 100 | 0 | 0 | 4 | 4 | Preparation of solum |  |  |  |  | 4 | 4 | Preparation of solum
[11 empty] | 4.1 | a) all materials | m2 | 20 | 544 | 10880 |  | 4.1 | a) all materials | m2 | 20 | 7500 | 150000
|  |  | 4 | 4 | Preparation of solum | [5 empty] | 4.2 | b) extra over for rock | m2 | 20 | 326.4 | 6528 |  | 4.2 | b) extra over for rock | m2 | 20 | 4500 | 90000
|  |  |  | 4.1 | a) all materials | m2 | 20 | 7364 | 147280
|  |  |  | 4.2 | b) extra over for rock | m2 | 20 | 736.4 | 14728 | 5 | 5 | Drilling & Grouting |  |  |  |  | 5 | 5 | Drilling & Grouting
[11 empty] | 5.1 | (a) Curtain grouting | m drill | 440 | 0 | 0 |  | 5.1 | (a) Curtain grouting | m drill | 440 | 0 | 0
|  |  | 5 | 5 | Drilling & Grouting | [5 empty] | 5.2 | (b) Consolidation grouting | m drill | 440 | 0 | 0 |  | 5.2 | (b) Consolidation grouting | m drill | 440 | 0 | 0
|  |  |  | 5.1 | (a) Curtain grouting | m drill | 440 | 0 | 0 |  | 5.3 | (c) Jet grouting | m drill | 4370 | 0 | 0 |  | 5.3 | (c) Jet grouting | m drill | 4370 | 0 | 0
|  |  |  | 5.2 | (b) Consolidation grouting | m drill | 440 | 0 | 0
|  |  |  | 5.3 | (c) Jet grouting | m drill | 4370 | 8700 | 38019000 | 6 | 6 | Embankment |  |  |  |  | 6 | 6 | Embankment
[11 empty] | 6.1 | (a) Earthfill | m3 | 50 | 457.2 | 22860 |  | 6.1 | (a) Earthfill | m3 | 50 | 6000 | 300000
|  |  | 6 | 6 | Embankment | [5 empty] | 6.2 | (b) Filters | m3 | 180 |  | 0 |  | 6.2 | (b) Filters | m3 | 180 | 1050 | 189000
|  |  |  | 6.1 | (a) Earthfill | m3 | 50 | 1050 | 52500 |  | 6.3 | (c) Rip-rap | m3 | 100 | 274.32 | 27432 |  | 6.3 | (c) Rip-rap | m3 | 100 | 3600 | 360000
|  |  |  | 6.2 | (b) Filters | m3 | 180 | 183.75 | 33075 |  | 6.4 | (d) Overhaul beyond 5km | m3.km | 10 | 0 | 0 |  | 6.4 | (d) Overhaul beyond 5km | m3.km | 10 | 0 | 0
|  |  |  | 6.3 | (c) Rip-rap | m3 | 100 | 4803 | 480300 | [8 empty] | 6.5 | (e) Waterproof Membrane System | m2 | 100 | 1400 | 140000
|  |  |  | 6.4 | (d) Geofabric | m2 | 30 | 3694 | 110820 | 7 | 7 | Concrete works
|  |  |  | 6.5 | (e) Overhaul beyond 5km | m3.km | 10 | 0 | 0 |  | 7.1 | a) Formwork |  |  |  |  | 7 | 7 | Concrete works
[11 empty] | 7.1.1 | (i) Gang formed | m2 | 260 | 2029 | 527540 |  | 7.1 | a) Formwork
|  |  | 7 | 7 | Concrete works | [5 empty] | 7.1.2 | (ii) Intricate | m2 | 320 | 304.35 | 97392 |  | 7.1.1 | (i) Gang formed | m2 | 260 | 202.9 | 52754
|  |  |  | 7.1 | a) Formwork | [12 empty] | 7.1.2 | (ii) Intricate | m2 | 320 | 30.435 | 9739.2
|  |  |  | 7.1.1 | (i) Gang formed | m2 | 260 | 6793 | 1766180 |  | 7.2 | (b)Concrete
|  |  |  | 7.1.2 | (ii) Intricate | m2 | 320 | 509.475 | 163032 |  | 7.2.1 | (i) Mass | m3 | 1740 | 70.2 | 122148 |  | 7.2 | (b)Concrete
[11 empty] | 7.2.2 | (ii) Structural | m3 | 2230 | 936 | 2087280 |  | 7.2.1 | (i) Mass | m3 | 1740 | 7.02 | 12214.8
|  |  |  | 7.2 | (b)Concrete | [12 empty] | 7.2.2 | (ii) Structural | m3 | 2230 | 93.6 | 208728
|  |  |  | 7.2.1 | (i) Mass | m3 | 1740 | 4805 | 8360700 |  | 7.3 | (c) Reinforcing | t | 18570 | 51.48 | 955983.6
|  |  |  | 7.2.2 | (ii) Structural | m3 | 2230 | 1054 | 2350420 | [8 empty] | 7.3 | (c) Reinforcing | t | 18570 | 5.148 | 95598.36
[12 empty] | SUB-TOTAL |  |  |  | 4170237.6
|  |  |  | 7.3 | (c) Reinforcing | t | 18570 | 57.97 | 1076502.9 | [9 empty] | SUB-TOTAL |  |  |  | 5946964.36
[10 empty] | 8 | 8 | Mechanical Items
[5 empty] | SUB-TOTAL |  |  |  | 53267131.9 |  | 8.1 | (a) Pipes, Valves & Gates | Sum | 1350000 | 1 | 1350000 | 8 | 8 | Mechanical Items
[11 empty] | 8.2 | (b) Cranes & hoists | Sum | 300000 | 1 | 300000 |  | 8.1 | (a) Pipes, Valves & Screens | Sum | 1090000 | 1 | 1090000
|  |  | 8 | 8 | Mechanical Items | [5 empty] | 8.3 | (c) Structural steelwork | t | 19630 | 10 | 196300 |  | 8.2 | (b) Cranes & hoists | Sum | 300000 | 1 | 300000
|  |  |  | 8.1 | (a) Pipes, Valves, Screens & Gates | Sum | 1450000 | 1 | 1450000 | [8 empty] | 8.3 | (c) Structural steelwork | t | 19630 | 6 | 117780
|  |  |  | 8.2 | (b) Cranes & hoists | Sum | 300000 | 1 | 300000 | 9 | 9 | Fencing | km | 27480 | 1.2485 | 34309.5532
|  |  |  | 8.3 | (c) Structural steelwork | t | 19630 | 5 | 98150 | [7 empty] | 9 | 9 | Fencing | km | 27480 | 1.6 | 43968
|  |  |  | 8.4 | (d) Low lift abstraction pumps | Sum | 11250000 | 1 | 11250000 | 10 | 10 | Landscaping (% of 1-9) | % | 5 |  | 208511.88
[17 empty] | 10 | 10 | Landscaping (% of 1-9) | % | 5 |  | 297348.218
|  |  | 9 | 9 | Fencing | km | 27480 | 1.8485 | 50797.5532 | 11 | 11 | Miscellaneous (% of 1-9) | % | 10 |  | 417023.76
[17 empty] | 11 | 11 | Miscellaneous (% of 1-9) | % | 10 |  | 594696.436
|  |  | 10 | 10 | Landscaping (% of 1-9) | % | 5 |  | 2663356.595 |  |  | SUB TOTAL A |  |  |  | 6676382.7932
[19 empty] | SUB TOTAL A |  |  |  | 8390757.014
|  |  | 11 | 11 | Miscellaneous (% of 1-9) | % | 10 |  | 5326713.19 | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 1669095.6983
[17 empty] | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 2097689.2535
[5 empty] | SUB TOTAL A |  |  |  | 74406149.2382 | 13 | 13 | Preliminary works
[11 empty] | 13.1 | (a) Access road | km | 235480 | 0.2 | 47096 | 13 | 13 | Preliminary works
|  |  | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 18601537.3096 |  | 13.2 | (b) Electricity to site | Sum | 150000 | 1 | 150000 |  | 13.1 | (a) Access road | km | 235480 | 0.2 | 47096
[11 empty] | 13.3 | (c) Water to site-construction (not potable) | Sum | 75000 | 1 | 75000 |  | 13.2 | (b) Electricity to site | Sum | 250000 | 1 | 250000
|  |  | 13 | 13 | Preliminary works | [5 empty] | 13.4 | (d) Railhead & materials handling | Sum | 0 | 1 | 0 |  | 13.3 | (c) Water to site-construction (not potable) | Sum | 50000 | 1 | 50000
|  |  |  | 13.1 | (a) Access road | km | 235480 | 0.5 | 117740 | [8 empty] | 13.4 | (d) Railhead & materials handling | Sum | 0 | 1 | 0
|  |  |  | 13.2 | (b) Electricity to site | Sum | 125000 | 1 | 125000 | 14 | 14 | Accomodation | Sum | 0 | 1 | 0
|  |  |  | 13.3 | (c) Water to site-construction (not potable) | Sum | 50000 | 1 | 50000 | [7 empty] | 14 | 14 | Accomodation | Sum | 0 | 1 | 0
|  |  |  | 13.4 | (d) Railhead & materials handling | Sum | 0 | 1 | 0 |  |  | SUB TOTAL B |  |  |  | 8617574.4915
[19 empty] | SUB TOTAL B |  |  |  | 10835542.2675
|  |  | 14 | 14 | Accomodation | Sum | 0 | 1 | 0 | 15 | 15 | Contingencies | % | 30 |  | 2585272.3475
[12 empty] | (% of sub total B) |  |  |  |  | 15 | 15 | Contingencies | % | 30 |  | 3250662.6803
[5 empty] | SUB TOTAL B |  |  |  | 93300426.5478 | [9 empty] | (% of sub total B)
[12 empty] | SUB TOTAL C (Civils Total) |  |  |  | 11202846.839
|  |  | 15 | 15 | Contingencies | % | 30 |  | 27990127.9643 | [9 empty] | SUB TOTAL C (Civils Total) |  |  |  | 14086204.9478
[5 empty] | (% of sub total B) |  |  |  |  | 16 | 16 | Planning design & supervision | % | 15 |  | 1680427.0258
[12 empty] | (% of sub-total C) |  |  |  |  | 16 | 16 | Planning design & supervision | % | 15 |  | 2112930.7422
[5 empty] | SUB TOTAL C (Civils Total) |  |  |  | 121290554.5121 | [9 empty] | (% of sub-total C)
[12 empty] | SUB TOTAL D |  |  |  | 12883273.8648
|  |  | 16 | 16 | Planning design & supervision | % | 15 |  | 18193583.1768 | [9 empty] | SUB TOTAL D |  |  |  | 16199135.6899
[5 empty] | (% of sub-total C) |  |  |  |  | 17 | 17 | VAT
[12 empty] | (% of sub-total D) | % | 14 |  | 1803658.3411 | 17 | 17 | VAT
[5 empty] | SUB TOTAL D |  |  |  | 139484137.6889 | [9 empty] | (% of sub-total D) | % | 14 |  | 2267878.9966
[12 empty] | NETT PROJECT COST |  |  |  | 14686932.2059
|  |  | 17 | 17 | VAT | [13 empty] | NETT PROJECT COST |  |  |  | 18467014.6865
[5 empty] | (% of sub-total D) | % | 14 |  | 19527779.2764
[10 empty] | 18 | 18 | Cost of relocations | Sum | 0 | 1 | 0
[5 empty] | NETT PROJECT COST |  |  |  | 159011916.9654 | [7 empty] | 18 | 18 | Cost of relocations | Sum | 0 | 1 | 0
[10 empty] | 19 | 19 | Cost of land acquisition | Sum | 0 | 1 | 0
[17 empty] | 19 | 19 | Cost of land acquisition | Sum | 0 | 1 | 0
|  |  | 18 | 18 | Cost of relocations | Sum | 0 | 1 | 0 |  |  | TOTAL PROJECT COST |  |  |  | 14686932.2059
[19 empty] | TOTAL PROJECT COST |  |  |  | 18467014.6865
|  |  | 19 | 19 | Cost of land acquisition | Sum | 0 | 1 | 0
[5 empty] | TOTAL PROJECT COST |  |  |  | 159011916.9654
|  |  | ABSTRACTION WEIR COST MODEL | [6 empty] | ABSTRACTION WEIR COST MODEL | [6 empty] | ABSTRACTION WEIR COST MODEL
|  |  | Mokolo Weir | [6 empty] | Mokolo De-Silting Works | [6 empty] | Mokolo Balancing Dam
|  |  | CIVIL ONLY | [6 empty] | CIVIL ONLY | [6 empty] | CIVIL ONLY
[5 empty] | SUB-TOTAL |  |  |  | 53267131.9 |  |  | SUB-TOTAL |  |  |  | 4170237.6 |  |  | SUB-TOTAL |  |  |  | 5946964.36
|  |  | 9 | 9 | Fencing | km | 27480 | 1.8485 | 50797.5532 | 9 | 9 | Fencing | km | 27480 | 1.2485 | 34309.5532 | 9 | 9 | Fencing | km | 27480 | 1.6 | 43968
|  |  | 10 | 10 | Landscaping (% of 1-7 & 9) | % | 5 |  | 2665896.4727 | 10 | 10 | Landscaping (% of 1-7 & 9) | % | 5 |  | 210227.3577 | 10 | 10 | Landscaping (% of 1-7 & 9) | % | 5 |  | 299546.618
|  |  | 11 | 11 | Miscellaneous (% of 1-7 & 9) | % | 10 |  | 5331792.9453 | 11 | 11 | Miscellaneous (% of 1-7 & 9) | % | 10 |  | 420454.7153 | 11 | 11 | Miscellaneous (% of 1-7 & 9) | % | 10 |  | 599093.236
[5 empty] | SUB TOTAL A |  |  |  | 61315618.8712 |  |  | SUB TOTAL A |  |  |  | 4835229.2262 |  |  | SUB TOTAL A |  |  |  | 6889572.214
|  |  | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 15328904.7178 | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 1208807.3065 | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 1722393.0535
|  |  | 13 | 13 | Preliminary works |  |  |  |  | 13 | 13 | Preliminary works |  |  |  |  | 13 | 13 | Preliminary works
|  |  |  | 13.1 | (a) Access road | km | 235480 | 0.5 | 117740 |  | 13.1 | (a) Access road | km | 235480 | 0.2 | 47096 |  | 13.1 | (a) Access road | km | 235480 | 0.2 | 47096
|  |  |  | 13.2 | (b) Electricity to site | Sum | 125000 | 1 | 125000 |  | 13.2 | (b) Electricity to site | Sum | 150000 | 1 | 150000 |  | 13.2 | (b) Electricity to site | Sum | 250000 | 1 | 250000
|  |  |  | 13.3 | (c) Water to site-construction (not potable) | Sum | 50000 | 1 | 50000 |  | 13.3 | (c) Water to site-construction (not potable) | Sum | 75000 | 1 | 75000 |  | 13.3 | (c) Water to site-construction (not potable) | Sum | 50000 | 1 | 50000
|  |  |  | 13.4 | (d) Railhead & materials handling | Sum | 0 | 1 | 0 |  | 13.4 | (d) Railhead & materials handling | Sum | 0 | 1 | 0 |  | 13.4 | (d) Railhead & materials handling | Sum | 0 | 1 | 0
|  |  | 14 | 14 | Accomodation | Sum | 0 | 1 | 0 | 14 | 14 | Accomodation | Sum | 0 | 1 | 0 | 14 | 14 | Accomodation | Sum | 0 | 1 | 0
[5 empty] | SUB TOTAL B |  |  |  | 76937263.589 |  |  | SUB TOTAL B |  |  |  | 6316132.5327 |  |  | SUB TOTAL B |  |  |  | 8959061.2675
|  |  | 15 | 15 | Contingencies | % | 30 |  | 23081179.0767 | 15 | 15 | Contingencies | % | 30 |  | 1894839.7598 | 15 | 15 | Contingencies | % | 30 |  | 2687718.3802
[5 empty] | (% of sub total B) | [6 empty] | (% of sub total B) | [6 empty] | (% of sub total B)
[5 empty] | SUB TOTAL C (Civils Total) |  |  |  | 100018442.6657 |  |  | SUB TOTAL C (Civils Total) |  |  |  | 8210972.2926 |  |  | SUB TOTAL C (Civils Total) |  |  |  | 11646779.6477
|  |  | 16 | 16 | Planning design & supervision | % | 15 |  | 15002766.3999 | 16 | 16 | Planning design & supervision | % | 15 |  | 1231645.8439 | 16 | 16 | Planning design & supervision | % | 15 |  | 1747016.9472
[5 empty] | (% of sub-total C) | [6 empty] | (% of sub-total C) | [6 empty] | (% of sub-total C)
[5 empty] | SUB TOTAL D |  |  |  | 115021209.0656 |  |  | SUB TOTAL D |  |  |  | 9442618.1365 |  |  | SUB TOTAL D |  |  |  | 13393796.5949
|  |  | MECHANICAL ONLY | [6 empty] | MECHANICAL ONLY | [6 empty] | MECHANICAL ONLY
|  |  | 8 | 8 | Mechanical Items |  |  |  |  | 8 | 8 | Mechanical Items |  |  |  |  | 8 | 8 | Mechanical Items
|  |  |  | 8.1 | (a) Pipes, Valves, Screens & Gates | Sum | 1450000 | 1 | 1450000 |  | 8.1 | (a) Pipes, Valves, Screens & Gates | Sum | 1350000 | 1 | 1350000 |  | 8.1 | (a) Pipes, Valves, Screens & Gates | Sum | 1090000 | 1 | 1090000
|  |  |  | 8.2 | (b) Cranes & hoists | Sum | 300000 | 1 | 300000 |  | 8.2 | (b) Cranes & hoists | Sum | 300000 | 1 | 300000 |  | 8.2 | (b) Cranes & hoists | Sum | 300000 | 1 | 300000
|  |  |  | 8.3 | (c) Structural steelwork | t | 19630 | 5 | 98150 |  | 8.3 | (c) Structural steelwork | t | 19630 | 10 | 196300 |  | 8.3 | (c) Structural steelwork | t | 19630 | 6 | 117780
|  |  |  | 8.4 | (d) Abstraction pumps | Sum | 11250000 | 1 | 11250000
[10 empty] | 10 | 10 | Landscaping (% of 8) | % | 5 |  | 92315 | 10 | 10 | Landscaping (% of 8) | % | 5 |  | 75389
|  |  | 10 | 10 | Landscaping (% of 8) | % | 5 |  | 654907.5
[10 empty] | 11 | 11 | Miscellaneous (% of 8) | % | 10 |  | 184630 | 11 | 11 | Miscellaneous (% of 8) | % | 10 |  | 150778
|  |  | 11 | 11 | Miscellaneous (% of 8) | % | 10 |  | 1309815
[12 empty] | SUB TOTAL A |  |  |  | 2123245 |  |  | SUB TOTAL A |  |  |  | 1733947
[5 empty] | SUB TOTAL A |  |  |  | 15062872.5
[10 empty] | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 530811.25 | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 433486.75
|  |  | 12 | 12 | Preliminary & General (% of sub-total A) | % | 25 |  | 3765718.125
[12 empty] | SUB TOTAL B |  |  |  | 2654056.25 |  |  | SUB TOTAL B |  |  |  | 2167433.75
[5 empty] | SUB TOTAL B |  |  |  | 18828590.625
[10 empty] | 15 | 15 | Contingencies | % | 30 |  | 796216.875 | 15 | 15 | Contingencies | % | 30 |  | 650230.125
|  |  | 15 | 15 | Contingencies | % | 30 |  | 5648577.1875 |  |  | (% of sub total B) | [6 empty] | (% of sub total B)
(% of sub total B)
[12 empty] | SUB TOTAL C (Mechanical Total) |  |  |  | 3450273.125 |  |  | SUB TOTAL C (Mechanical Total) |  |  |  | 2817663.875
[5 empty] | SUB TOTAL C (Mechanical Total) |  |  |  | 24477167.8125
[10 empty] | 16 | 16 | Planning design & supervision | % | 15 |  | 517540.9688 | 16 | 16 | Planning design & supervision | % | 15 |  | 422649.5812
|  |  | 16 | 16 | Planning design & supervision | % | 15 |  | 3671575.1719 |  |  | (% of sub-total C) | [6 empty] | (% of sub-total C)
(% of sub-total C)
[12 empty] | SUB TOTAL D |  |  |  | 3967814.0938 |  |  | SUB TOTAL D |  |  |  | 3240313.4562
[5 empty] | SUB TOTAL D |  |  |  | 28148742.9844
Note on I63: njordaan: R45 million for the transfer scheme weir abstraction which has 8 pumps Therefore approximately 2/8 x R45 million for the Mokolo Weir abstraction which has 2 pumps
Note on I152: njordaan: R45 million for the transfer scheme weir abstraction which has 8 pumps Therefore approximately 2/8 x R45 million for the Mokolo Weir abstraction which has 2 pumps

## Sum Tot Cost
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008
RATES: |  | April 2008
SUMMARY OF TOTAL PROJECT COST CALCULATIONS | [6 empty] | P1 | P1 | P4 | P4 | P5 | P5 | P6 | P6
No | Pay Ref | Description |  |  | Unit | Rate | Quantity | Amount | Amount | AMOUNT | QUANTITY | AMOUNT | QUANTITY | AMOUNT
Rands
Construction Costs
1 |  | Diameter pipeline : | 2300 | mm | m | 1 | 0 | 0 | 0
|  |  | 2200 | mm | m | 1 | 0 | 0 | 0
|  |  | 1700 | mm | m | 1 | 0 | 0 | #REF!
|  |  | 1500 | mm | m | 1 | 0 | 0 | #REF!
|  |  | 1000 | mm | m | 1 | 25394 | 180127649.6382 | 180127649.6382
|  |  | 900 | mm | m | 1 | 0 | 0 | 0
|  |  | 800 | mm | m | 1 | 37834 | 252364904.2875 | 252364904.2875
|  |  | 700 | mm | m | 1 | 0 | 0 | #REF!
|  |  | 600 | mm | m | 1 | 0 | 0 | 0
|  |  | 500 | mm | m | 1 | 0 | 0 | 0
2 |  | Pump Station |  |  | No | 1 | 1 | 45569274.0147
Other 2
Other 3
|  | SUB-TOTAL A | [5 empty] | 478061827.9403
3 |  | Landscaping & EIA Remediation (% of Sub-total A) |  |  | % | 5 |  | 23903091.397
4 |  | Miscellaneous (% of Sub-total A) |  |  | % | 10 |  | 47806182.794
|  | SUB TOTAL B | [5 empty] | 549771102.1314
5 |  | Preliminary & General (% of Sub-total B) |  |  | % | 30 |  | 164931330.6394
To include below
6 |  | Preliminary works
|  | (a) Access road |  |  | km | 350000 | 63.228 | 22129800
|  | (b) Electricity to site |  |  | Sum
|  | (c) Water to site - construction |  |  | Sum
(not potable)
|  | (d) Railhead & materials handling |  |  | Sum
9. |  | Accommodation |  |  | Sum
|  | SUB TOTAL C | [5 empty] | 736832232.7708
7 |  | Contingencies
|  | (% of Sub-total C) |  |  | % | 20 |  | 147366446.5542
|  | SUB TOTAL D | [5 empty] | 884198679.3249 |  | 0 |  | 0 |  | 0
8. |  | Weir Abstraction Works all costs included |  |  | sum | 1 |  | 121290554.5121 | [6 empty] | 139484137.6889
|  | Weir Siltation Works all costs included |  |  | sum | 1 |  | 11202846.839 | [6 empty] | 12883273.8648
|  | Weir Balancing Dam all costs included |  |  | sum | 1 |  | 14086204.9478 | [6 empty] | 16199135.6899
|  | SUB TOTAL E | [5 empty] | 1030778285.6238 |  | 0 |  | 0 |  | 0
9 |  | Planning design & supervision
|  | (% of Sub-total D) |  |  | % | 15 |  | 154616742.8436 |  | 0 |  | 0 |  | 0
|  | SUB TOTAL F | [5 empty] | 1185395028.4673 |  | 0 |  | 0 |  | 0
10 |  | Cost of ESKOM transmission lines to site |  |  | Sum | 1 | 1 | 131220100
11 |  | VAT (% of sub total E) |  |  | % | 14 |  | 184326117.9854 |  | 0 |  | 0 |  | 0
|  | NETT PROJECT COST | [5 empty] | 1500941246.4527 |  | 0 |  | 0 |  | 0
12 |  | Cost of relocations |  |  | Sum |  |  | 0 |  | 0 |  | 0 |  | 0
13 |  | Cost of land acquisition |  |  | Sum |  |  | 10000000 |  | 0 |  | 0 |  | 0
14 |  | Cost Environmental Impact Assessment |  |  | Sum |  |  | 500000
|  | TOTAL RISING MAIN COST | [5 empty] | 1511441246.4527 |  | 0 |  | 0 |  | 0
|  | TOTAL RISING MAIN COST (EXCL VAT) | [5 empty] | 1327115128.4673 |  | 0 |  | 0 |  | 0 | 1481731871.3109
Note on D44: User: Include in P&G percentage
Note on J71: njordaan: Revised cost figures from KV3 electrical department (Rudolph Evert) to supply full redundancy from two sources = R 119,291,000 (excl VAT) + 10% fees

## Econ Mod
Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study | [25 empty] | Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan | [25 empty] | Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
BASE YEAR: |  | 2008 | [23 empty] | BASE YEAR: |  | 2008
RATES: |  | April 2008 | [23 empty] | RATES: |  | April 2008
ECONOMIC COST MODEL | [25 empty] | ECONOMIC COST MODEL
YEAR | RAW WATER COST | LOSSES TO BE AUGMENTED FROM CROCODILE TRANSFER SCHEME | Environmental & Social Impacts | EXISTING EXXARO PIPELINES |  | EXISTING PUMP STATION |  |  | WEIR COST |  |  | RISING MAIN COSTS - 1000 |  | RISING MAIN COSTS - 800 |  | GRAVITY MAIN COSTS - 700 |  | GRAVITY MAIN COSTS - 500 |  | PUMP STATION COSTS |  |  |  | ESKOM ELECTRISITY TO SITE |  | YEAR | TOTAL ANNUAL COST MOKOLO TRANSFER SYSTEM | [5 empty] | TOTAL ANNUAL COST COMBINED SCHEME |  | PRESENT VALUE OF COST (2008) AT 6% |  | PRESENT VALUE OF COST (2008) AT 8% |  | PRESENT VALUE OF COST (2008) AT 10%
|  |  |  | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE CIVIL | MAINTENANCE E&M | CAPITAL | MAINTENANCE CIVIL | MAINTENANCE E&M | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE CIVIL | MAINTENANCE E&M | ELECTRICITY |  |  |  | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION | CAPITAL | MAINTENANCE & OPERATION
| 2 | 4.5 |  |  | 0.5% |  | 0.25% | 4% |  | 0.25% | 4% |  | 0.5% |  | 0.5% |  | 0.5% |  | 0.5% |  | 0.25% | 4% | [13 empty] | 6% |  | 8% |  | 10%
2008 | [22 empty] | 0 |  |  | 2008 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | [22 empty] | 0 |  |  | 2009 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 |  |  | 10500000 | 33005644.5097 |  | 7959331.743 |  |  | 86607247.1656 |  |  | 191943327.9842 |  | 269463928.0177 |  | 0 |  | 0 |  | 47006984.6099 |  |  | 0 | 65610050 | 0 | 2010 | 712096514.0302 | 0 |  |  |  |  | 712096514.0302 | 0 | 633763362.4334 | 0 | 610507985.2796 | 0 | 588509515.7274 | 0
2011 | 51748593.727 | 21617483.8384 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 | 86607247.1656 |  |  | 191943327.9842 |  | 269463928.0177 |  | 0 | 0 | 0 | 0 | 47006984.6099 |  |  | 5585599.946 | 65610050 | 1 | 2011 | 660631537.7775 | 79345536.5215 |  |  |  |  | 660631537.7775 | 79345536.5215 | 554678978.0973 | 66620042.486 | 524430614.1225 | 62987045.0718 | 496342252.2746 | 59613475.9741
2012 | 71610763.1408 | 29914716.5818 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 8825346.6294 |  | 2 | 2012 | 0 | 118724912.9822 |  |  |  |  | 0 | 118724912.9822 | 0 | 94041251.2417 | 0 | 87266355.3125 | 0 | 81090713.0539
2013 | 101259033.2445 | 42300000 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 13359932.1678 |  | 3 | 2013 | 0 | 165293052.0425 |  |  |  |  | 0 | 165293052.0425 | 0 | 123516584.0568 | 0 | 112495673.8066 | 0 | 102633980.5667
2014 | 93040151.9851 | 38866640.3665 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 13359932.1678 |  | 4 | 2014 | 0 | 153640811.1497 |  |  |  |  | 0 | 153640811.1497 | 0 | 108310709.2617 | 0 | 96819772.6362 | 0 | 86726232.4863
2015 | 70012637.7126 | 29247114.8534 |  | 64110684 | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10408453.9926 |  | 5 | 2015 | 64110684 | 118042293.1888 |  |  |  |  | 64110684 | 118042293.1888 | 42637266.4534 | 78504866.7935 | 37407968.3477 | 68876544.3104 | 32898917.9599 | 60574361.0444
2016 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 6 | 2016 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 77265222.2453 | 0 | 66533586.7445 | 0 | 57449929.3565
2017 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 7 | 2017 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 72891719.0993 | 0 | 61605172.9116 | 0 | 52227208.5059
2018 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 8 | 2018 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 68765772.7352 | 0 | 57041826.77 | 0 | 47479280.4599
2019 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 9 | 2019 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 64873370.5049 | 0 | 52816506.2685 | 0 | 43162982.2363
2020 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 10 | 2020 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 61201292.9292 | 0 | 48904172.4709 | 0 | 39239074.7603
2021 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 11 | 2021 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 57737068.8011 | 0 | 45281641.1767 | 0 | 35671886.1457
2022 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 12 | 2022 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 54468932.8312 | 0 | 41927445.534 | 0 | 32428987.4052
2023 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 13 | 2023 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 51385785.6898 | 0 | 38821708.8278 | 0 | 29480897.6411
2024 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 14 | 2024 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 48477156.3112 | 0 | 35946026.6924 | 0 | 26800816.0373
2025 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 | 1915617.3307 | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 15 | 2025 | 1915617.3307 | 123149025.7039 |  |  |  |  | 1915617.3307 | 123149025.7039 | 711392.1163 | 45733166.3313 | 517731.8873 | 33283358.0485 | 378994.6765 | 24364378.2158
2026 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 16 | 2026 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 43144496.539 | 0 | 30817924.119 | 0 | 22149434.7416
2027 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 17 | 2027 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 40702355.2254 | 0 | 28535114.925 | 0 | 20135849.7651
2028 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 18 | 2028 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 38398448.3259 | 0 | 26421402.7083 | 0 | 18305317.9683
2029 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 19 | 2029 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 36224951.2508 | 0 | 24464261.767 | 0 | 16641198.153
2030 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 20 | 2030 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 34174482.3121 | 0 | 22652094.2287 | 0 | 15128361.9572
2031 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 21 | 2031 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 32240077.6529 | 0 | 20974161.3228 | 0 | 13753056.3248
2032 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 22 | 2032 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 30415167.5971 | 0 | 19420519.7434 | 0 | 12502778.4771
2033 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 23 | 2033 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 28693554.3369 | 0 | 17981962.7253 | 0 | 11366162.2519
2034 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 24 | 2034 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 27069390.8839 | 0 | 16649965.4864 | 0 | 10332874.7744
2035 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 25 | 2035 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 25537161.2112 | 0 | 15416634.7097 | 0 | 9393522.5222
2036 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 26 | 2036 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 24091661.52 | 0 | 14274661.7682 | 0 | 8539565.9293
2037 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 27 | 2037 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 22727982.566 | 0 | 13217279.415 | 0 | 7763241.7539
2038 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 28 | 2038 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 21441492.9868 | 0 | 12238221.6806 | 0 | 7057492.5035
2039 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 29 | 2039 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 20227823.5725 | 0 | 11331686.7413 | 0 | 6415902.2759
2040 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 | 1915617.3307 | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 30 | 2040 | 1915617.3307 | 123149025.7039 |  |  |  |  | 1915617.3307 | 123149025.7039 | 296839.0746 | 19082852.4269 | 163210.6829 | 10492302.5382 | 90728.3123 | 5832638.4327
2041 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 31 | 2041 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 18002690.9687 | 0 | 9715094.9428 | 0 | 5302398.5752
2042 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 32 | 2042 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 16983670.7252 | 0 | 8995458.2804 | 0 | 4820362.3411
2043 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 33 | 2043 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 16022330.8728 | 0 | 8329128.0374 | 0 | 4382147.5828
2044 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 34 | 2044 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 15115406.4838 | 0 | 7712155.5901 | 0 | 3983770.5298
2045 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 35 | 2045 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 14259817.4376 | 0 | 7140884.8057 | 0 | 3621609.5725
2046 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 36 | 2046 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 13452657.96 | 0 | 6611930.3756 | 0 | 3292372.3387
2047 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 37 | 2047 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 12691186.7547 | 0 | 6122157.7552 | 0 | 2993065.7624
2048 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 38 | 2048 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 11972817.6931 | 0 | 5668664.5882 | 0 | 2720968.8749
2049 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 39 | 2049 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 11295111.0312 | 0 | 5248763.5076 | 0 | 2473608.0681
2050 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 40 | 2050 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 10655765.1238 | 0 | 4859966.2107 | 0 | 2248734.6074
2051 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 41 | 2051 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 10052608.6074 | 0 | 4499968.7136 | 0 | 2044304.1885
2052 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 42 | 2052 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 9483593.0258 | 0 | 4166637.6978 | 0 | 1858458.3532
2053 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 43 | 2053 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 8946785.8734 | 0 | 3857997.8683 | 0 | 1689507.5938
2054 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 44 | 2054 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 8440364.0315 | 0 | 3572220.2485 | 0 | 1535915.9944
2055 | 73334405.1953 | 30634751.6895 |  |  | 165028.2225 |  | 5969.4988 | 222861.2888 |  | 344644.0595 | 1414274.8214 |  | 1669072.4173 |  | 2343164.5915 |  | 0 |  | 0 |  | 70731.9582 | 2138339.7723 | 10805782.1888 |  | 45 | 2055 | 0 | 123149025.7039 |  |  |  |  | 0 | 123149025.7039 | 0 | 7962607.5769 | 0 | 3307611.3412 | 0 | 1396287.2676
TOTAL | 3321047387.6232 | 1387336023.2199 | 10500000 | 97116328.5097 | 7426270.0147 | 7959331.743 | 268627.4463 | 10028757.9962 | 173214494.3313 | 15164338.6177 |  | 383886655.9685 | 73439186.3592 | 538927856.0355 | 103099242.0242 | 0 | 0 | 0 | 0 | 97845203.881 | 3112206.1602 | 94086949.9815 | 483770552.4559 | 131220100 |  | TOTAL | 1440669970.469 | 5561007634.0395 |  |  |  |  | 1440669970.469 | 5561007634.0395 | 1232087838.1749 | 1703302253.8916 | 1173027510.32 | 1285303670.4243 | 1118220408.9508 | 1008625113.3706
NET PRESENT COST
[33 empty] | Discounted to 2008 at 6% |  | 2935390092.0665
[33 empty] | Discounted to 2008 at 8% |  | 2458331180.7443
[33 empty] | Discounted to 2008 at 10% |  | 2126845522.3213
Note on D14: njordaan: R500,000 for EIA R3,020,585 for land acquisition (servitudes)
Note on E14: njordaan: Value to purchase existing pipeline infrastructure. Value copied from 8-P1A-MD-IDA and pasted here since the cost will be the same for both Mokolo Dam and River Bend Weir options.
Note on G14: njordaan: Value to purchase existing pipeline infrastructure. Value copied from 8-P1A-MD-IDA and pasted here since the cost will be the same for both Mokolo Dam and River Bend Weir options.
Note on Y14: njordaan: Cost from KV3 electrical department = R 19,537,313 (excl VAT)
Note on Y15: njordaan: Cost from KV3 electrical department = R 19,537,313 (excl VAT)

## URV Calculator
| PROJECT: |  | Mokolo and Crocodile (West) Water Augmentation Project Feasibility Study
| OPTION: |  | Scenario 8, Phase 1A - New Pipeline from Rivers Bend Weir to Maimba T-off and Steenbokpan
| BASE YEAR: |  | 2008
| RATES: |  | April 2008
UNIT REFERENCE VALUE CALCULATIONS AT DIFFERENT DISCOUNT RATES
| Year | Net Demand | Total annual costs | Discounted to 2008 at 6% |  | Discounted to 2008 at 8% |  | Discounted to 2008 at 10%
|  | Mm³ | (excl VAT) | Use | Costs | Use | Costs | Use | Costs
| 2008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2010 | 0 | 712096514.0302 | 0 | 633763362.4334 | 0 | 610507985.2796 | 0 | 588509515.7274
| 2011 | 20.2522 | 739977074.299 | 17.0042 | 621299020.5833 | 16.0769 | 587417659.1943 | 15.2158 | 555955728.2487
| 2012 | 28.0254 | 118724912.9822 | 22.1988 | 94041251.2417 | 20.5995 | 87266355.3125 | 19.1418 | 81090713.0539
| 2013 | 36.7 | 165293052.0425 | 27.4244 | 123516584.0568 | 24.9774 | 112495673.8066 | 22.7878 | 102633980.5667
0 | 2014 | 36.7 | 153640811.1497 | 25.8721 | 108310709.2617 | 23.1272 | 96819772.6362 | 20.7162 | 86726232.4863
1 | 2015 | 27.4 | 182152977.1888 | 18.2226 | 121142133.2469 | 15.9876 | 106284512.6581 | 14.0605 | 93473279.0043
2 | 2016 | 28.7 | 123149025.7039 | 18.0067 | 77265222.2453 | 15.5057 | 66533586.7445 | 13.3888 | 57449929.3565
3 | 2017 | 28.7 | 123149025.7039 | 16.9875 | 72891719.0993 | 14.3571 | 61605172.9116 | 12.1716 | 52227208.5059
4 | 2018 | 28.7 | 123149025.7039 | 16.0259 | 68765772.7352 | 13.2937 | 57041826.77 | 11.0651 | 47479280.4599
5 | 2019 | 28.7 | 123149025.7039 | 15.1188 | 64873370.5049 | 12.3089 | 52816506.2685 | 10.0592 | 43162982.2363
6 | 2020 | 28.7 | 123149025.7039 | 14.263 | 61201292.9292 | 11.3972 | 48904172.4709 | 9.1447 | 39239074.7603
7 | 2021 | 28.7 | 123149025.7039 | 13.4557 | 57737068.8011 | 10.5529 | 45281641.1767 | 8.3134 | 35671886.1457
8 | 2022 | 28.7 | 123149025.7039 | 12.694 | 54468932.8312 | 9.7712 | 41927445.534 | 7.5576 | 32428987.4052
9 | 2023 | 28.7 | 123149025.7039 | 11.9755 | 51385785.6898 | 9.0474 | 38821708.8278 | 6.8706 | 29480897.6411
10 | 2024 | 28.7 | 123149025.7039 | 11.2976 | 48477156.3112 | 8.3773 | 35946026.6924 | 6.246 | 26800816.0373
11 | 2025 | 28.7 | 125064643.0345 | 10.6582 | 46444558.4476 | 7.7567 | 33801089.9358 | 5.6781 | 24743372.8923
12 | 2026 | 28.7 | 123149025.7039 | 10.0549 | 43144496.539 | 7.1821 | 30817924.119 | 5.1619 | 22149434.7416
13 | 2027 | 28.7 | 123149025.7039 | 9.4857 | 40702355.2254 | 6.6501 | 28535114.925 | 4.6927 | 20135849.7651
14 | 2028 | 28.7 | 123149025.7039 | 8.9488 | 38398448.3259 | 6.1575 | 26421402.7083 | 4.2661 | 18305317.9683
15 | 2029 | 28.7 | 123149025.7039 | 8.4423 | 36224951.2508 | 5.7014 | 24464261.767 | 3.8782 | 16641198.153
16 | 2030 | 28.7 | 123149025.7039 | 7.9644 | 34174482.3121 | 5.2791 | 22652094.2287 | 3.5257 | 15128361.9572
17 | 2031 | 28.7 | 123149025.7039 | 7.5136 | 32240077.6529 | 4.888 | 20974161.3228 | 3.2052 | 13753056.3248
18 | 2032 | 28.7 | 123149025.7039 | 7.0883 | 30415167.5971 | 4.526 | 19420519.7434 | 2.9138 | 12502778.4771
19 | 2033 | 28.7 | 123149025.7039 | 6.6871 | 28693554.3369 | 4.1907 | 17981962.7253 | 2.6489 | 11366162.2519
20 | 2034 | 28.7 | 123149025.7039 | 6.3085 | 27069390.8839 | 3.8803 | 16649965.4864 | 2.4081 | 10332874.7744
21 | 2035 | 28.7 | 123149025.7039 | 5.9515 | 25537161.2112 | 3.5929 | 15416634.7097 | 2.1892 | 9393522.5222
22 | 2036 | 28.7 | 123149025.7039 | 5.6146 | 24091661.52 | 3.3267 | 14274661.7682 | 1.9902 | 8539565.9293
23 | 2037 | 28.7 | 123149025.7039 | 5.2968 | 22727982.566 | 3.0803 | 13217279.415 | 1.8092 | 7763241.7539
24 | 2038 | 28.7 | 123149025.7039 | 4.997 | 21441492.9868 | 2.8521 | 12238221.6806 | 1.6448 | 7057492.5035
25 | 2039 | 28.7 | 123149025.7039 | 4.7141 | 20227823.5725 | 2.6409 | 11331686.7413 | 1.4952 | 6415902.2759
26 | 2040 | 28.7 | 125064643.0345 | 4.4473 | 19379691.5015 | 2.4452 | 10655513.2211 | 1.3593 | 5923366.745
27 | 2041 | 28.7 | 123149025.7039 | 4.1955 | 18002690.9687 | 2.2641 | 9715094.9428 | 1.2357 | 5302398.5752
28 | 2042 | 28.7 | 123149025.7039 | 3.9581 | 16983670.7252 | 2.0964 | 8995458.2804 | 1.1234 | 4820362.3411
29 | 2043 | 28.7 | 123149025.7039 | 3.734 | 16022330.8728 | 1.9411 | 8329128.0374 | 1.0213 | 4382147.5828
30 | 2044 | 28.7 | 123149025.7039 | 3.5227 | 15115406.4838 | 1.7973 | 7712155.5901 | 0.92842 | 3983770.5298
31 | 2045 | 28.7 | 123149025.7039 | 3.3233 | 14259817.4376 | 1.6642 | 7140884.8057 | 0.84402 | 3621609.5725
32 | 2046 | 28.7 | 123149025.7039 | 3.1352 | 13452657.96 | 1.5409 | 6611930.3756 | 0.76729 | 3292372.3387
33 | 2047 | 28.7 | 123149025.7039 | 2.9577 | 12691186.7547 | 1.4268 | 6122157.7552 | 0.69754 | 2993065.7624
34 | 2048 | 28.7 | 123149025.7039 | 2.7903 | 11972817.6931 | 1.3211 | 5668664.5882 | 0.63412 | 2720968.8749
35 | 2049 | 28.7 | 123149025.7039 | 2.6323 | 11295111.0312 | 1.2232 | 5248763.5076 | 0.57648 | 2473608.0681
36 | 2050 | 28.7 | 123149025.7039 | 2.4833 | 10655765.1238 | 1.1326 | 4859966.2107 | 0.52407 | 2248734.6074
37 | 2051 | 28.7 | 123149025.7039 | 2.3428 | 10052608.6074 | 1.0487 | 4499968.7136 | 0.47643 | 2044304.1885
38 | 2052 | 28.7 | 123149025.7039 | 2.2102 | 9483593.0258 | 0.97104 | 4166637.6978 | 0.43312 | 1858458.3532
39 | 2053 | 28.7 | 123149025.7039 | 2.0851 | 8946785.8734 | 0.89911 | 3857997.8683 | 0.39374 | 1689507.5938
40 | 2054 | 28.7 | 123149025.7039 | 1.967 | 8440364.0315 | 0.83251 | 3572220.2485 | 0.35795 | 1535915.9944
41 | 2055 | 28.7 | 123149025.7039 | 1.8557 | 7962607.5769 | 0.77084 | 3307611.3412 | 0.32541 | 1396287.2676
42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL | 1297.0777 | 7001677604.5084 | 397.9127 | 2935390092.0665 | 300.4603 | 2458331180.7443 | 235.9444 | 2126845522.3213
| URV |  |  |  | 7.377 |  | 8.1819 |  | 9.0142
UNIT REFERENCE VALUE CALCULATIONS AT DIFFERENT DISCOUNTED RATES- 30 year analysis period (2014-2044)
| TOTAL | 981.3777 | 5647038321.7659 | 370.1299 | 2816176776.9511 | 287.6293 | 2403274377.6319 | 229.9142 | 2100970689.6997
| URV |  |  |  | 7.6086 |  | 8.3555 |  | 9.1381
UNIT REFERENCE VALUE CALCULATIONS AT DIFFERENT DISCOUNTED RATES- 20 year analysis period (2014-2034)
| TOTAL | 694.3777 | 4413632447.3966 | 323.6984 | 2616646864.5426 | 261.5922 | 2291388543.2456 | 215.1176 | 2037388918.941
| URV |  |  |  | 8.0836 |  | 8.7594 |  | 9.471

## PS Costs
TOTAL CAPITAL COST FOR PUMPING STATIONS
(March 2003, excluding VAT)
DWAF - 2003 | [10 empty] | Escalated
PS Capacity | Total Cost | M+E Cost | Civil Cost |  | Mechanical Cost |  | Electrical Cost |  |  | E of M | Total Cost Esclated at 10% pa | Cost /kW | Civil (30%) | E&M (70%)
kW | Million Rand | Million Rand | Million Rand | % of Total | Million Rand | % of Total | Million Rand | % of Total |  |  | Million Rand
100 | 1876900 | 1179900 | 697000 | 37.14% | 786600 | 41.91% | 393300 | 20.95% | 18769 | 50% | 3022766.219 | 30227.6622 | 9068.2987 | 21159.3635
200 | 3108700 | 1984300 | 1124400 | 36.17% | 1322900 | 42.55% | 661400 | 21.28% | 15543.5 | 50% | 5006592.437 | 25032.9622 | 7509.8887 | 17523.0735
300 | 4177000 | 2689600 | 1487400 | 35.61% | 1793000 | 42.93% | 896500 | 21.46% | 13923.3333 | 50% | 6727100.27 | 22423.6676 | 6727.1003 | 15696.5673
400 | 5151200 | 3337200 | 1814000 | 35.22% | 2224800 | 43.19% | 1112400 | 21.59% | 12878 | 50% | 8296059.112 | 20740.1478 | 6222.0443 | 14518.1034
500 | 6061200 | 3945200 | 2116000 | 34.91% | 2630100 | 43.39% | 1315100 | 21.7% | 12122.4 | 50% | 9761623.212 | 19523.2464 | 5856.9739 | 13666.2725
600 | 6923000 | 4523300 | 2399700 | 34.66% | 3015500 | 43.56% | 1507800 | 21.78% | 11538.3333 | 50% | 11149560.73 | 18582.6012 | 5574.7804 | 13007.8209
700 | 7746700 | 5077700 | 2669000 | 34.45% | 3385100 | 43.7% | 1692600 | 21.85% | 11066.7143 | 50% | 12476137.817 | 17823.054 | 5346.9162 | 12476.1378
800 | 8539100 | 5612500 | 2926600 | 34.27% | 3741700 | 43.82% | 1870800 | 21.91% | 10673.875 | 50% | 13752305.941 | 17190.3824 | 5157.1147 | 12033.2677
900 | 9305200 | 6130900 | 3174300 | 34.11% | 4087300 | 43.92% | 2043600 | 21.96% | 10339.1111 | 50% | 14986117.652 | 16651.2418 | 4995.3726 | 11655.8693
1000 | 10048700 | 6635000 | 3413700 | 33.97% | 4423300 | 44.02% | 2211700 | 22.01% | 10048.7 | 50% | 16183531.837 | 16183.5318 | 4855.0596 | 11328.4723
2000 | 16665900 | 11158700 | 5507200 | 33.04% | 7439100 | 44.64% | 3719600 | 22.32% | 8332.95 | 50% | 26840598.609 | 13420.2993 | 4026.0898 | 9394.2095
3000 | 22409600 | 15124500 | 7285100 | 32.51% | 10083000 | 44.99% | 5041500 | 22.5% | 7469.8667 | 50% | 36090884.896 | 12030.295 | 3609.0885 | 8421.2065
5000 | 32549200 | 22185500 | 10363700 | 31.84% | 14790300 | 45.44% | 7395200 | 22.72% | 6509.84 | 50% | 52420812.092 | 10484.1624 | 3145.2487 | 7338.9137
6000 | 37189300 | 25436300 | 11753000 | 31.6% | 16957600 | 45.6% | 8478800 | 22.8% | 6198.2167 | 50% | 59893739.543 | 9982.2899 | 2994.687 | 6987.6029
7000 | 41625800 | 28553800 | 13072000 | 31.4% | 19035900 | 45.73% | 9517900 | 22.87% | 5946.5429 | 50% | 67038767.158 | 9576.9667 | 2873.09 | 6703.8767
8000 | 45895200 | 31561600 | 14333600 | 31.23% | 21041000 | 45.85% | 10520500 | 22.92% | 5736.9 | 50% | 73914678.552 | 9239.3348 | 2771.8004 | 6467.5344
9000 | 50023700 | 34476500 | 15547200 | 31.08% | 22984300 | 45.95% | 11492200 | 22.97% | 5558.1889 | 50% | 80563669.087 | 8951.5188 | 2685.4556 | 6266.0632
10000 | 54030900 | 37311400 | 16719500 | 30.94% | 24874200 | 46.04% | 12437100 | 23.02% | 5403.09 | 50% | 87017304.759 | 8701.7305 | 2610.5191 | 6091.2113
20000 | 89723300 | 62750000 | 26973300 | 30.06% | 41833300 | 46.62% | 20916700 | 23.31% | 4486.165 | 50% | 144500271.883 | 7225.0136 | 2167.5041 | 5057.5095
40000 | 149048000 | 105532400 | 43515600 | 29.2% | 70355000 | 47.2% | 35177500 | 23.6% | 3726.2 | 50% | 240043294.48 | 6001.0824 | 1800.3247 | 4200.7577
50000 | 175517000 | 124758000 | 50759000 | 28.92% | 83172000 | 47.39% | 41586000 | 23.69% | 3510.34 | 50% | 282671883.67 | 5653.4377 | 1696.0313 | 3957.4064
60000 | 200602700 | 143039000 | 57563700 | 28.7% | 95359300 | 47.54% | 47679700 | 23.77% | 3343.3783 | 50% | 323072654.377 | 5384.5442 | 1615.3633 | 3769.181
70000 | 224593800 | 160570000 | 64023800 | 28.51% | 107046700 | 47.66% | 53523300 | 23.83% | 3208.4829 | 50% | 361710560.838 | 5167.2937 | 1550.1881 | 3617.1056
80000 | 247686800 | 177483700 | 70203100 | 28.34% | 118322500 | 47.77% | 59161200 | 23.89% | 3096.085 | 50% | 398902068.268 | 4986.2759 | 1495.8828 | 3490.3931
90000 | 270022300 | 193875500 | 76146800 | 28.2% | 129250300 | 47.87% | 64625200 | 23.93% | 3000.2478 | 50% | 434873614.373 | 4831.929 | 1449.5787 | 3382.3503
100000 | 291705800 | 209817100 | 81888700 | 28.07% | 139878100 | 47.95% | 69939000 | 23.98% | 2917.058 | 50% | 469795107.958 | 4697.9511 | 1409.3853 | 3288.5658
10%
VKE E&M Costs
Power Absorb (kW) | Rand (Million) 2006 | Million Rand/kW | 20% Escalated
30 | 100000 | 3333.3333 | 4000
100 | 500000 | 5000 | 6000
950 | 12000000 | 12631.5789 | 15157.8947
2000 | 23000000 | 11500 | 13800
5000 | 40000000 | 8000 | 9600
10000 | 60000000 | 6000 | 7200
22800 | 88000000 | 3859.6491 | 4631.5789
40200 | 115000000 | 2860.6965 | 3432.8358
70000 | 155000000 | 2214.2857 | 2657.1429 | [11 empty] | Installed kW | 12300
[15 empty] | Cost/kW | 8244.1862
[15 empty] | Total Cost | 101403490.4875
Alex Bell
|  |  | Total | E&M Only
Siviel – R 26,806,796.05 |  |  | 26806796.05 | [5 empty] | 157.3%
Meganies – R 78,853,523.49 |  |  | 78853523.49 | 78853523.49
Elektries – R 17,039,759.05 |  |  | 17039759.05 | 17039759.05
|  |  | 122700078.59 | 95893282.54
KVA |  |  | 24 |  | MVA
MW |  |  | 23.04 |  | MW
kW |  |  | 23040 | 23040
|  |  | 5325.5242 | 4162.0348 | R/KW (Total)
Totale koste – R 1,680,061,891.19 |  |  | 1690061891.19
Pyplyn koste – R 579,799,368.48 |  |  | 579799368.48 | 34.31%

## Excvation Vol
[23 empty] | 500 |  |  | 600 |  |  | 700 |  |  | 800 |  |  | 900 |  |  | 1000 |  |  | 1100 |  |  | 1200 |  |  | 1300 |  |  | 1400 |  |  | 1500 |  |  | 1600 |  |  | 1700 |  |  | 1800 |  |  | 1900 |  |  | 2000 |  |  | 2100 |  |  | 2200 |  |  | 2300 |  |  | 2400 |  |  | 2500
Typical Trench Geometry
Side Allowance |  | mm | 500 | for D up to 2000
|  |  | 600 | for D > 2000
Bedding thickness |  | mm | 300
Selected Fill Over Pipe |  | mm | 300
Batter angle (from vertical) |  | deg | 15
Min Cover |  | mm | 1300 | for D up to 1500
|  |  | 1800 | for D > 1500
% Intermediate Excavation |  |  | 0%
% Hard Excvation |  |  | 40%
% Bedding from trench |  |  | 30%
% Bedding Cradle & Fill blanket from trench |  |  | 30%
[23 empty] | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry |  |  | Trench Geometry
Qty Volumes per linear meter | [22 empty] | ND | mm | 500 | ND | mm | 600 | ND | mm | 700 | ND | mm | 800 | ND | mm | 900 | ND | mm | 1000 | ND | mm | 1100 | ND | mm | 1200 | ND | mm | 1300 | ND | mm | 1400 | ND | mm | 1500 | ND | mm | 1600 | ND | mm | 1700 | ND | mm | 1800 | ND | mm | 1900 | ND | mm | 2000 | ND | mm | 2100 | ND | mm | 2200 | ND | mm | 2300 | ND | mm | 2400 | ND | mm | 2500
[23 empty] | OD | mm | 510 | OD | mm | 610 | OD | mm | 711 | OD | mm | 813 | OD | mm | 914 | OD | mm | 1016 | OD | mm | 1118 | OD | mm | 1219 | OD | mm | 1321 | OD | mm | 1422 | OD | mm | 1524 | OD | mm | 1626 | OD | mm | 1727 | OD | mm | 1829 | OD | mm | 1930 | OD | mm | 2032 | OD | mm | 2134 | OD | mm | 2236 | OD | mm | 2337 | OD | mm | 2450 | OD | mm | 2540
Pipe ND | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 2500 | 1 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 500 | Side Allowance | mm | 600 | Side Allowance | mm | 600 | Side Allowance | mm | 600 | Side Allowance | mm | 600 | Side Allowance | mm | 600 | Side Allowance | mm | 600
[22 empty] | 2 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300 | Bedding thickness | mm | 300
[22 empty] | 3 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300 | Selected Fill Over Pipe | mm | 300
Excavation | [21 empty] | 4 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15 | Batter angle (from vertical) | deg | 15
Soft & Intermediate | 3.834 | 4.2483 | 4.6885 | 5.1551 | 5.639 | 6.1497 | 6.6827 | 7.2324 | 7.8095 | 8.4029 | 10.9058 | 11.614 | 12.3371 | 13.0895 | 13.8564 | 15.4794 | 16.3186 | 17.18 | 18.0548 | 19.0594 | 19.879 | 5 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1300 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800 | Min Cover | mm | 1800
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
Hard | 1.5336 | 1.6993 | 1.8754 | 2.062 | 2.2556 | 2.4599 | 2.6731 | 2.8929 | 3.1238 | 3.3612 | 4.3623 | 4.6456 | 4.9348 | 5.2358 | 5.5426 | 6.1918 | 6.5274 | 6.872 | 7.2219 | 7.6238 | 7.9516 | 7
Bedding | [21 empty] | 8 | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0% | % Intermediate Excavation |  | 0%
From trench | 0.1359 | 0.1449 | 0.15399 | 0.16317 | 0.17226 | 0.18144 | 0.19062 | 0.19971 | 0.20889 | 0.21798 | 0.22716 | 0.23634 | 0.24543 | 0.25461 | 0.2637 | 0.29088 | 0.30006 | 0.30924 | 0.31833 | 0.3285 | 0.3366 | 9 | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40% | % Hard Excvation |  | 40%
From commercial sources | 0.3171 | 0.3381 | 0.35931 | 0.38073 | 0.40194 | 0.42336 | 0.44478 | 0.46599 | 0.48741 | 0.50862 | 0.53004 | 0.55146 | 0.57267 | 0.59409 | 0.6153 | 0.67872 | 0.70014 | 0.72156 | 0.74277 | 0.7665 | 0.7854 | 10
[22 empty] | 11 | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30% | % Bedding from trench |  | 30%
Cradle & Fill Blanket | [21 empty] | 12 | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30% | % Bedding Cradle & Fill blanket from trench |  | 30%
From trench | 0.33041 | 0.38128 | 0.43438 | 0.48975 | 0.54631 | 0.60518 | 0.66581 | 0.72757 | 0.7917 | 0.85693 | 0.92455 | 0.99393 | 1.0644 | 1.1372 | 1.2111 | 1.4274 | 1.5117 | 1.5977 | 1.6846 | 1.7839 | 1.8645 | 13
From commercial sources | 0.77095 | 0.88965 | 1.0135 | 1.1427 | 1.2747 | 1.4121 | 1.5535 | 1.6977 | 1.8473 | 1.9995 | 2.1573 | 2.3192 | 2.4835 | 2.6536 | 2.826 | 3.3307 | 3.5273 | 3.728 | 3.9308 | 4.1624 | 4.3505 | 14
15
Main Fill | [21 empty] | 16 |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter |  |  | per meter
From trench | 2.0754 | 2.2022 | 2.3302 | 2.4596 | 2.5876 | 2.717 | 2.8463 | 2.9743 | 3.1037 | 3.2317 | 5.2426 | 5.4366 | 5.6287 | 5.8227 | 6.0148 | 6.5087 | 6.7027 | 6.8967 | 7.0888 | 7.3038 | 7.4749 | 17
[22 empty] | 18 | Base Width |  | 1.51 | Base Width |  | 1.61 | Base Width |  | 1.711 | Base Width |  | 1.813 | Base Width |  | 1.914 | Base Width |  | 2.016 | Base Width |  | 2.118 | Base Width |  | 2.219 | Base Width |  | 2.321 | Base Width |  | 2.422 | Base Width |  | 2.524 | Base Width |  | 2.626 | Base Width |  | 2.727 | Base Width |  | 2.829 | Base Width |  | 2.93 | Base Width |  | 3.232 | Base Width |  | 3.334 | Base Width |  | 3.436 | Base Width |  | 3.537 | Base Width |  | 3.65 | Base Width |  | 3.74
Spoil | 1.2923 | 1.52 | 1.7699 | 2.0426 | 2.3328 | 2.6462 | 2.98 | 3.3307 | 3.7053 | 4.0963 | 4.5115 | 4.9471 | 5.3987 | 5.875 | 6.3668 | 7.2523 | 7.8041 | 8.3763 | 8.9631 | 9.6433 | 10.203 | 19 | Trench top width |  | 2.3433 | Trench top width |  | 2.4701 | Trench top width |  | 2.5982 | Trench top width |  | 2.7275 | Trench top width |  | 2.8556 | Trench top width |  | 2.9849 | Trench top width |  | 3.1142 | Trench top width |  | 3.2423 | Trench top width |  | 3.3716 | Trench top width |  | 3.4997 | Trench top width |  | 3.897 | Trench top width |  | 4.0263 | Trench top width |  | 4.1544 | Trench top width |  | 4.2837 | Trench top width |  | 4.4118 | Trench top width |  | 4.7411 | Trench top width |  | 4.8704 | Trench top width |  | 4.9998 | Trench top width |  | 5.1278 | Trench top width |  | 5.2711 | Trench top width |  | 5.3852
[23 empty] | Trench width at top of blanket |  | 1.8074 | Trench width at top of blanket |  | 1.9342 | Trench width at top of blanket |  | 2.0623 | Trench width at top of blanket |  | 2.1916 | Trench width at top of blanket |  | 2.3197 | Trench width at top of blanket |  | 2.449 | Trench width at top of blanket |  | 2.5783 | Trench width at top of blanket |  | 2.7064 | Trench width at top of blanket |  | 2.8357 | Trench width at top of blanket |  | 2.9638 | Trench width at top of blanket |  | 3.0931 | Trench width at top of blanket |  | 3.2225 | Trench width at top of blanket |  | 3.3505 | Trench width at top of blanket |  | 3.4798 | Trench width at top of blanket |  | 3.6079 | Trench width at top of blanket |  | 3.9372 | Trench width at top of blanket |  | 4.0666 | Trench width at top of blanket |  | 4.1959 | Trench width at top of blanket |  | 4.324 | Trench width at top of blanket |  | 4.4672 | Trench width at top of blanket |  | 4.5814
Check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Pipe Area |  | 0.20428 | Pipe Area |  | 0.29225 | Pipe Area |  | 0.39704 | Pipe Area |  | 0.51912 | Pipe Area |  | 0.65612 | Pipe Area |  | 0.81073 | Pipe Area |  | 0.98169 | Pipe Area |  | 1.1671 | Pipe Area |  | 1.3706 | Pipe Area |  | 1.5881 | Pipe Area |  | 1.8241 | Pipe Area |  | 2.0765 | Pipe Area |  | 2.3425 | Pipe Area |  | 2.6273 | Pipe Area |  | 2.9255 | Pipe Area |  | 3.2429 | Pipe Area |  | 3.5767 | Pipe Area |  | 3.9268 | Pipe Area |  | 4.2895 | Pipe Area |  | 4.7144 | Pipe Area |  | 5.0671
[23 empty] | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m | trench excavation: |  | Vol/m
[23 empty] | in soft material |  | 3.834 | in soft material |  | 4.2483 | in soft material |  | 4.6885 | in soft material |  | 5.1551 | in soft material |  | 5.639 | in soft material |  | 6.1497 | in soft material |  | 6.6827 | in soft material |  | 7.2324 | in soft material |  | 7.8095 | in soft material |  | 8.4029 | in soft material |  | 10.9058 | in soft material |  | 11.614 | in soft material |  | 12.3371 | in soft material |  | 13.0895 | in soft material |  | 13.8564 | in soft material |  | 15.4794 | in soft material |  | 16.3186 | in soft material |  | 17.18 | in soft material |  | 18.0548 | in soft material |  | 19.0594 | in soft material |  | 19.879
[23 empty] | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0 | extra over for intermediate material |  | 0
| 0.20428 | 0.29225 | 0.39704 | 0.51912 | 0.65612 | 0.81073 | 0.98169 | 1.1671 | 1.3706 | 1.5881 | 1.8241 | 2.0765 | 2.3425 | 2.6273 | 2.9255 | 3.2429 | 3.5767 | 3.9268 | 4.2895 | 4.7144 | 5.0671 |  | extra over for hard (rock) material |  | 1.5336 | extra over for hard (rock) material |  | 1.6993 | extra over for hard (rock) material |  | 1.8754 | extra over for hard (rock) material |  | 2.062 | extra over for hard (rock) material |  | 2.2556 | extra over for hard (rock) material |  | 2.4599 | extra over for hard (rock) material |  | 2.6731 | extra over for hard (rock) material |  | 2.8929 | extra over for hard (rock) material |  | 3.1238 | extra over for hard (rock) material |  | 3.3612 | extra over for hard (rock) material |  | 4.3623 | extra over for hard (rock) material |  | 4.6456 | extra over for hard (rock) material |  | 4.9348 | extra over for hard (rock) material |  | 5.2358 | extra over for hard (rock) material |  | 5.5426 | extra over for hard (rock) material |  | 6.1918 | extra over for hard (rock) material |  | 6.5274 | extra over for hard (rock) material |  | 6.872 | extra over for hard (rock) material |  | 7.2219 | extra over for hard (rock) material |  | 7.6238 | extra over for hard (rock) material |  | 7.9516
[23 empty] | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding: |  |  | bedding:
[23 empty] | from trench |  | 0.1359 | from trench |  | 0.1449 | from trench |  | 0.15399 | from trench |  | 0.16317 | from trench |  | 0.17226 | from trench |  | 0.18144 | from trench |  | 0.19062 | from trench |  | 0.19971 | from trench |  | 0.20889 | from trench |  | 0.21798 | from trench |  | 0.22716 | from trench |  | 0.23634 | from trench |  | 0.24543 | from trench |  | 0.25461 | from trench |  | 0.2637 | from trench |  | 0.29088 | from trench |  | 0.30006 | from trench |  | 0.30924 | from trench |  | 0.31833 | from trench |  | 0.3285 | from trench |  | 0.3366
[23 empty] | from commercial sources/import |  | 0.3171 | from commercial sources/import |  | 0.3381 | from commercial sources/import |  | 0.35931 | from commercial sources/import |  | 0.38073 | from commercial sources/import |  | 0.40194 | from commercial sources/import |  | 0.42336 | from commercial sources/import |  | 0.44478 | from commercial sources/import |  | 0.46599 | from commercial sources/import |  | 0.48741 | from commercial sources/import |  | 0.50862 | from commercial sources/import |  | 0.53004 | from commercial sources/import |  | 0.55146 | from commercial sources/import |  | 0.57267 | from commercial sources/import |  | 0.59409 | from commercial sources/import |  | 0.6153 | from commercial sources/import |  | 0.67872 | from commercial sources/import |  | 0.70014 | from commercial sources/import |  | 0.72156 | from commercial sources/import |  | 0.74277 | from commercial sources/import |  | 0.7665 | from commercial sources/import |  | 0.7854
[23 empty] | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket: |  |  | Cradle and fill blanket:
[23 empty] | from trench |  | 0.33041 | from trench |  | 0.38128 | from trench |  | 0.43438 | from trench |  | 0.48975 | from trench |  | 0.54631 | from trench |  | 0.60518 | from trench |  | 0.66581 | from trench |  | 0.72757 | from trench |  | 0.7917 | from trench |  | 0.85693 | from trench |  | 0.92455 | from trench |  | 0.99393 | from trench |  | 1.0644 | from trench |  | 1.1372 | from trench |  | 1.2111 | from trench |  | 1.4274 | from trench |  | 1.5117 | from trench |  | 1.5977 | from trench |  | 1.6846 | from trench |  | 1.7839 | from trench |  | 1.8645
[23 empty] | from commercial sources |  | 0.77095 | from commercial sources |  | 0.88965 | from commercial sources |  | 1.0135 | from commercial sources |  | 1.1427 | from commercial sources |  | 1.2747 | from commercial sources |  | 1.4121 | from commercial sources |  | 1.5535 | from commercial sources |  | 1.6977 | from commercial sources |  | 1.8473 | from commercial sources |  | 1.9995 | from commercial sources |  | 2.1573 | from commercial sources |  | 2.3192 | from commercial sources |  | 2.4835 | from commercial sources |  | 2.6536 | from commercial sources |  | 2.826 | from commercial sources |  | 3.3307 | from commercial sources |  | 3.5273 | from commercial sources |  | 3.728 | from commercial sources |  | 3.9308 | from commercial sources |  | 4.1624 | from commercial sources |  | 4.3505
[23 empty] | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill |  |  | Main Fill
[23 empty] | from trench |  | 2.0754 | from trench |  | 2.2022 | from trench |  | 2.3302 | from trench |  | 2.4596 | from trench |  | 2.5876 | from trench |  | 2.717 | from trench |  | 2.8463 | from trench |  | 2.9743 | from trench |  | 3.1037 | from trench |  | 3.2317 | from trench |  | 5.2426 | from trench |  | 5.4366 | from trench |  | 5.6287 | from trench |  | 5.8227 | from trench |  | 6.0148 | from trench |  | 6.5087 | from trench |  | 6.7027 | from trench |  | 6.8967 | from trench |  | 7.0888 | from trench |  | 7.3038 | from trench |  | 7.4749
[23 empty] | Spoil |  | 1.2923 | Spoil |  | 1.52 | Spoil |  | 1.7699 | Spoil |  | 2.0426 | Spoil |  | 2.3328 | Spoil |  | 2.6462 | Spoil |  | 2.98 | Spoil |  | 3.3307 | Spoil |  | 3.7053 | Spoil |  | 4.0963 | Spoil |  | 4.5115 | Spoil |  | 4.9471 | Spoil |  | 5.3987 | Spoil |  | 5.875 | Spoil |  | 6.3668 | Spoil |  | 7.2523 | Spoil |  | 7.8041 | Spoil |  | 8.3763 | Spoil |  | 8.9631 | Spoil |  | 9.6433 | Spoil |  | 10.203
[23 empty] | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0 | Check |  | 0
Excavation
Soft
Intermediate
Hard
Bedding
From trench
From commercial sources
Cradle & Fill Blanket
From trench
From commercial sources
Main Fill
From trench
Spoil
Check
D
200
D/2
D/2
Min Cover
Side
ø
D
200
D/2
D/2
Min Cover
Side
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
D
200
D/2
D/2
Min Cover
Side
ø
D
200
D/2
D/2
Min Cover
Side
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
D
200
D/2
D/2
Min Cover
Side
ø
D
200
D/2
D/2
Min Cover
Side
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
D
200
D/2
D/2
Min Cover
Side
ø
D
200
D/2
D/2
Min Cover
Side
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
D
200
D/2
D/2
Min Cover
Side
ø
D
200
D/2
D/2
Min Cover
Side
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
D
200
D/2
D/2
Min Cover
Side
ø
D
200
D/2
D/2
Min Cover
Side
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
D
200
D/2
D/2
Min Cover
Side
ø
D
200
D/2
D/2
Min Cover
Side
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø
300
D
D/2
D/2
Min Cover
Side
300
ø

## Pipe Material Cost
Pipe costs | [11 empty] | Calculated
[9 empty] | Rate (ex works) | E/O Delivery | Rate delivered | Steel vol/m | Mass (t)/m | Steel cost (R/m) | Coating Area/m | Coating cost | Rate (ex works) (R/m) | E/O Delivery | Rate delivered
Dia (nom) | Dia (OD) | Dia (ID) | Wall (t) | D/t | D/t (nominal) | Grade | Yeild (MPa) | Bar (working) |  |  |  |  | 7950 | 17500 |  | 200
500 | 508 | 498.7636 | 4.6182 |  | 110 | API Grade X42 | 290 | 32.8463 | 1335.2558 | 85 | 1420.2558 | 0.0073033 | 0.058061 | 1016.0699 | 1.5959 | 319.1858 | 1335.2558 | 85 | 1420.2558 | 0 | 0% |  | 17500
500 | 508 | 497.84 | 5.08 |  | 100 | API Grade X42 | 290 | 36.198 | 1435.8374 | 85 | 1520.8374 | 0.0080262 | 0.063809 | 1116.6515 | 1.5959 | 319.1858 | 1435.8374 | 85 | 1520.8374 | 0 | 0%
600 | 610 | 601.2857 | 4.3571 |  | 140 | API Grade X42 | 290 | 25.7058 | 1536.657 | 85 | 1621.657 | 0.0082903 | 0.065908 | 1153.3827 | 1.9164 | 383.2743 | 1536.657 | 85 | 1621.657 | 0 | 0%
600 | 610 | 600.6154 | 4.6923 |  | 130 | API Grade X42 | 290 | 27.7141 | 1624.6914 | 85 | 1709.6914 | 0.008923 | 0.070938 | 1241.4171 | 1.9164 | 383.2743 | 1624.6914 | 85 | 1709.6914 | 0 | 0%
600 | 610 | 599.8333 | 5.0833 |  | 120 | API Grade X42 | 290 | 30.0627 | 1727.2741 | 85 | 1812.2741 | 0.0096604 | 0.0768 | 1343.9998 | 1.9164 | 383.2743 | 1727.2741 | 85 | 1812.2741 | 0 | 0%
600 | 610 | 598.9091 | 5.5455 |  | 110 | API Grade X42 | 290 | 32.8463 | 1848.3358 | 85 | 1933.3358 | 0.010531 | 0.083718 | 1465.0615 | 1.9164 | 383.2743 | 1848.3358 | 85 | 1933.3358 | 0 | 0%
600 | 610 | 597.8 | 6.1 |  | 100 | API Grade X42 | 290 | 36.198 | 1993.3634 | 85 | 2078.3634 | 0.011573 | 0.092005 | 1610.0891 | 1.9164 | 383.2743 | 1993.3634 | 85 | 2078.3634 | 0 | 0%
700 | 711 | 700.8429 | 5.0786 |  | 140 | API Grade X42 | 290 | 25.7058 | 2013 | 85 | 2098 | 0.011263 | 0.08954 | 1566.9422 | 2.2337 | 446.7345 | 2013.6767 | 92 | 2105.6767 | -0.67669 | 0.03362%
700 | 711 | 700.0615 | 5.4692 |  | 130 | API Grade X42 | 290 | 27.7141 | 2109 | 85 | 2194 | 0.012122 | 0.096374 | 1686.5424 | 2.2337 | 446.7345 | 2133.2768 | 93 | 2226.2768 | -24.2768 | 1.151%
700 | 711 | 699.15 | 5.925 |  | 120 | API Grade X42 | 290 | 30.0627 | 2205 | 85 | 2290 | 0.013124 | 0.10434 | 1825.9073 | 2.2337 | 446.7345 | 2272.6418 | 94 | 2366.6418 | -67.6418 | 3.068%
700 | 711 | 698.0727 | 6.4636 |  | 110 | API Grade X42 | 290 | 32.8463 | 2349 | 85 | 2434 | 0.014306 | 0.11374 | 1990.3772 | 2.2337 | 446.7345 | 2437.1116 | 95 | 2532.1116 | -88.1116 | 3.751%
700 | 711 | 696.78 | 7.11 |  | 100 | API Grade X42 | 290 | 36.198 | 2501 | 85 | 2586 | 0.015723 | 0.12499 | 2187.4062 | 2.2337 | 446.7345 | 2634.1407 | 96 | 2730.1407 | -133.1407 | 5.323%
800 | 813 | 802.8375 | 5.0812 |  | 160 | API Grade X42 | 290 | 22.4519 | 2290 | 110 | 2400 | 0.012897 | 0.10253 | 1794.2927 | 2.5541 | 510.823 | 2305.1157 | 97 | 2402.1157 | -15.1157 | 0.6601%
800 | 813 | 802.16 | 5.42 |  | 150 | API Grade X42 | 290 | 23.9689 | 2373 | 110 | 2483 | 0.013751 | 0.10932 | 1913.1098 | 2.5541 | 510.823 | 2423.9327 | 98 | 2521.9327 | -50.9327 | 2.146%
800 | 813 | 801.3857 | 5.8071 |  | 140 | API Grade X42 | 290 | 25.7058 | 2482 | 110 | 2592 | 0.014726 | 0.11707 | 2048.7778 | 2.5541 | 510.823 | 2559.6008 | 99 | 2658.6008 | -77.6008 | 3.127%
800 | 813 | 800.4923 | 6.2538 |  | 130 | API Grade X42 | 290 | 27.7141 | 2620 | 110 | 2730 | 0.01585 | 0.12601 | 2205.1551 | 2.5541 | 510.823 | 2715.9781 | 100 | 2815.9781 | -95.9781 | 3.663%
800 | 813 | 799.45 | 6.775 |  | 120 | API Grade X42 | 290 | 30.0627 | 2757 | 110 | 2867 | 0.01716 | 0.13642 | 2387.3748 | 2.5541 | 510.823 | 2898.1978 | 101 | 2999.1978 | -141.1978 | 5.121%
800 | 813 | 798.2182 | 7.3909 |  | 110 | API Grade X42 | 290 | 32.8463 | 2921 | 110 | 3031 | 0.018706 | 0.14871 | 2602.4193 | 2.5541 | 510.823 | 3113.2423 | 102 | 3215.2423 | -192.2423 | 6.581%
800 | 813 | 796.74 | 8.13 |  | 100 | API Grade X42 | 290 | 36.198 | 3116 | 110 | 3226 | 0.020557 | 0.16343 | 2860.0349 | 2.5541 | 510.823 | 3370.8579 | 103 | 3473.8579 | -254.8579 | 8.179%
900 | 914 | 902.575 | 5.7125 |  | 160 | API Grade X42 | 290 | 22.4519 | 2743 | 135 | 2878 | 0.0163 | 0.12959 | 2267.7992 | 2.8714 | 574.2831 | 2842.0824 | 104 | 2946.0824 | -99.0824 | 3.612%
900 | 914 | 901.8133 | 6.0933 |  | 150 | API Grade X42 | 290 | 23.9689 | 2867 | 135 | 3002 | 0.01738 | 0.13817 | 2417.9716 | 2.8714 | 574.2831 | 2992.2547 | 105 | 3097.2547 | -125.2547 | 4.369%
900 | 914 | 900.9429 | 6.5286 |  | 140 | API Grade X42 | 290 | 25.7058 | 2990 | 135 | 3125 | 0.018612 | 0.14797 | 2589.4419 | 2.8714 | 574.2831 | 3163.725 | 106 | 3269.725 | -173.725 | 5.81%
900 | 914 | 899.9385 | 7.0308 |  | 130 | API Grade X42 | 290 | 27.7141 | 3144 | 135 | 3279 | 0.020033 | 0.15926 | 2787.0865 | 2.8714 | 574.2831 | 3361.3696 | 107 | 3468.3696 | -217.3696 | 6.914%
900 | 914 | 898.7667 | 7.6167 |  | 120 | API Grade X42 | 290 | 30.0627 | 3338 | 135 | 3473 | 0.021688 | 0.17242 | 3017.3932 | 2.8714 | 574.2831 | 3591.6764 | 108 | 3699.6764 | -253.6764 | 7.6%
900 | 914 | 897.3818 | 8.3091 |  | 110 | API Grade X42 | 290 | 32.8463 | 3557 | 135 | 3692 | 0.023642 | 0.18795 | 3289.187 | 2.8714 | 574.2831 | 3863.4702 | 109 | 3972.4702 | -306.4702 | 8.616%
900 | 914 | 895.72 | 9.14 |  | 100 | API Grade X42 | 290 | 36.198 | 3803 | 135 | 3938 | 0.025982 | 0.20656 | 3614.7864 | 2.8714 | 574.2831 | 4189.0695 | 110 | 4299.0695 | -386.0695 | 10.15%
1000 | 1016 | 1003.3 | 6.35 |  | 160 | API Grade X42 | 290 | 22.4519 | 3318 | 170 | 3488 | 0.020142 | 0.16013 | 2802.2032 | 3.1919 | 638.3716 | 3440.5748 | 111 | 3551.5748 | -122.5748 | 3.694%
1000 | 1016 | 1002.4533 | 6.7733 |  | 150 | API Grade X42 | 290 | 23.9689 | 3455 | 170 | 3625 | 0.021475 | 0.17073 | 2987.7635 | 3.1919 | 638.3716 | 3626.1351 | 112 | 3738.1351 | -171.1351 | 4.953%
1000 | 1016 | 1001.4857 | 7.2571 |  | 140 | API Grade X42 | 290 | 25.7058 | 3628 | 170 | 3798 | 0.022998 | 0.18284 | 3199.6406 | 3.1919 | 638.3716 | 3838.0122 | 113 | 3951.0122 | -210.0122 | 5.789%
1000 | 1016 | 1000.3692 | 7.8154 |  | 130 | API Grade X42 | 290 | 27.7141 | 3799 | 170 | 3969 | 0.024754 | 0.19679 | 3443.8599 | 3.1919 | 638.3716 | 4082.2315 | 114 | 4196.2315 | -283.2315 | 7.455%
1000 | 1016 | 999.0667 | 8.4667 |  | 120 | API Grade X42 | 290 | 30.0627 | 4044 | 170 | 4214 | 0.026799 | 0.21305 | 3728.4381 | 3.1919 | 638.3716 | 4366.8097 | 115 | 4481.8097 | -322.8097 | 7.982%
1000 | 1016 | 997.5273 | 9.2364 |  | 110 | API Grade X42 | 290 | 32.8463 | 4305 | 170 | 4475 | 0.029213 | 0.23224 | 4064.2798 | 3.1919 | 638.3716 | 4702.6514 | 116 | 4818.6514 | -397.6514 | 9.237%
1000 | 1016 | 995.68 | 10.16 |  | 100 | API Grade X42 | 290 | 36.198 | 4655 | 170 | 4825 | 0.032105 | 0.25523 | 4466.6062 | 3.1919 | 638.3716 | 5104.9778 | 117 | 5221.9778 | -449.9778 | 9.667%
1100 | 1118 | 1104.025 | 6.9875 |  | 160 | API Grade X42 | 290 | 22.4519 | 3869 | 225 | 4094 | 0.024389 | 0.19389 | 3393.0934 | 3.5123 | 702.4601 | 4095.5535 | 118 | 4213.5535 | -226.5535 | 5.856%
1100 | 1118 | 1103.0933 | 7.4533 |  | 150 | API Grade X42 | 290 | 23.9689 | 4059 | 225 | 4284 | 0.026004 | 0.20673 | 3617.7821 | 3.5123 | 702.4601 | 4320.2422 | 119 | 4439.2422 | -261.2422 | 6.436%
1100 | 1118 | 1102.0286 | 7.9857 |  | 140 | API Grade X42 | 290 | 25.7058 | 4253 | 225 | 4478 | 0.027848 | 0.22139 | 3874.3369 | 3.5123 | 702.4601 | 4576.797 | 120 | 4696.797 | -323.797 | 7.613%
1100 | 1118 | 1100.8 | 8.6 |  | 130 | API Grade X42 | 290 | 27.7141 | 4480 | 225 | 4705 | 0.029973 | 0.23829 | 4170.0538 | 3.5123 | 702.4601 | 4872.514 | 121 | 4993.514 | -392.514 | 8.761%
1100 | 1118 | 1099.3667 | 9.3167 |  | 120 | API Grade X42 | 290 | 30.0627 | 4756 | 225 | 4981 | 0.03245 | 0.25798 | 4514.64 | 3.5123 | 702.4601 | 5217.1001 | 122 | 5339.1001 | -461.1001 | 9.695%
1100 | 1118 | 1097.6727 | 10.1636 |  | 110 | API Grade X42 | 290 | 32.8463 | 5104 | 225 | 5329 | 0.035373 | 0.28122 | 4921.2994 | 3.5123 | 702.4601 | 5623.7595 | 123 | 5746.7595 | -519.7595 | 10.18%
1100 | 1118 | 1095.64 | 11.18 |  | 100 | API Grade X42 | 290 | 36.198 | 5482 | 225 | 5707 | 0.038875 | 0.30906 | 5408.4629 | 3.5123 | 702.4601 | 6110.923 | 124 | 6234.923 | -628.923 | 11.47%
1200 | 1219 | 1203.7625 | 7.6188 |  | 160 | API Grade X42 | 290 | 22.4519 | 4450 | 225 | 4675 | 0.028994 | 0.23051 | 4033.8488 | 3.8296 | 765.9203 | 4799.7691 | 125 | 4924.7691 | -349.7691 | 7.86%
1200 | 1219 | 1202.7467 | 8.1267 |  | 150 | API Grade X42 | 290 | 23.9689 | 4661 | 225 | 4886 | 0.030914 | 0.24577 | 4300.968 | 3.8296 | 765.9203 | 5066.8883 | 126 | 5192.8883 | -405.8883 | 8.708%
1200 | 1219 | 1201.5857 | 8.7071 |  | 140 | API Grade X42 | 290 | 25.7058 | 4909 | 225 | 5134 | 0.033107 | 0.2632 | 4605.9709 | 3.8296 | 765.9203 | 5371.8912 | 127 | 5498.8912 | -462.8912 | 9.429%
1200 | 1219 | 1200.2462 | 9.3769 |  | 130 | API Grade X42 | 290 | 27.7141 | 5238 | 225 | 5463 | 0.035634 | 0.28329 | 4957.5313 | 3.8296 | 765.9203 | 5723.4516 | 128 | 5851.4516 | -485.4516 | 9.268%
1200 | 1219 | 1198.6833 | 10.1583 |  | 120 | API Grade X42 | 290 | 30.0627 | 5575 | 225 | 5800 | 0.038578 | 0.3067 | 5367.1895 | 3.8296 | 765.9203 | 6133.1098 | 129 | 6262.1098 | -558.1098 | 10.01%
1200 | 1219 | 1196.8364 | 11.0818 |  | 110 | API Grade X42 | 290 | 32.8463 | 6059 | 225 | 6284 | 0.042053 | 0.33432 | 5850.6429 | 3.8296 | 765.9203 | 6616.5632 | 130 | 6746.5632 | -557.5632 | 9.202%
1200 | 1219 | 1194.62 | 12.19 |  | 100 | API Grade X42 | 290 | 36.198 | 6532 | 225 | 6757 | 0.046216 | 0.36742 | 6429.8028 | 3.8296 | 765.9203 | 7195.7231 | 131 | 7326.7231 | -663.7231 | 10.16%
1300 | 1321 | 1304.4875 | 8.2562 |  | 160 | API Grade X42 | 290 | 22.4519 | 5138 | 225 | 5363 | 0.03405 | 0.27069 | 4737.1577 | 4.15 | 830.0088 | 5567.1665 | 132 | 5699.1665 | -429.1665 | 8.353%
1300 | 1321 | 1303.3867 | 8.8067 |  | 150 | API Grade X42 | 290 | 23.9689 | 5392 | 225 | 5617 | 0.036304 | 0.28862 | 5050.8496 | 4.15 | 830.0088 | 5880.8584 | 133 | 6013.8584 | -488.8584 | 9.066%
1300 | 1321 | 1302.1286 | 9.4357 |  | 140 | API Grade X42 | 290 | 25.7058 | 5695 | 225 | 5920 | 0.038879 | 0.30909 | 5409.0303 | 4.15 | 830.0088 | 6239.0391 | 134 | 6373.0391 | -544.0391 | 9.553%
1300 | 1321 | 1300.6769 | 10.1615 |  | 130 | API Grade X42 | 290 | 27.7141 | 6061 | 225 | 6286 | 0.041846 | 0.33268 | 5821.8859 | 4.15 | 830.0088 | 6651.8947 | 135 | 6786.8947 | -590.8947 | 9.749%
1300 | 1321 | 1298.9833 | 11.0083 |  | 120 | API Grade X42 | 290 | 30.0627 | 6520 | 225 | 6745 | 0.045304 | 0.36017 | 6302.9688 | 4.15 | 830.0088 | 7132.9775 | 136 | 7268.9775 | -612.9775 | 9.401%
1300 | 1321 | 1296.9818 | 12.0091 |  | 110 | API Grade X42 | 290 | 32.8463 | 6927 | 225 | 7152 | 0.049385 | 0.39261 | 6870.7131 | 4.15 | 830.0088 | 7700.7219 | 137 | 7837.7219 | -773.7219 | 11.17%
1300 | 1321 | 1294.58 | 13.21 |  | 100 | API Grade X42 | 290 | 36.198 | 7399 | 225 | 7624 | 0.054274 | 0.43148 | 7550.8506 | 4.15 | 830.0088 | 8380.8594 | 138 | 8518.8594 | -981.8594 | 13.27%
1400 | 1422 | 1404.225 | 8.8875 |  | 160 | API Grade X42 | 290 | 22.4519 | 5823 | 225 | 6048 | 0.039455 | 0.31367 | 5489.2297 | 4.4673 | 893.469 | 6382.6986 | 139 | 6521.6986 | -559.6986 | 9.612%
1400 | 1422 | 1403.04 | 9.48 |  | 150 | API Grade X42 | 290 | 23.9689 | 6129 | 225 | 6354 | 0.042068 | 0.33444 | 5852.7233 | 4.4673 | 893.469 | 6746.1923 | 140 | 6886.1923 | -617.1923 | 10.07%
1400 | 1422 | 1401.6857 | 10.1571 |  | 140 | API Grade X42 | 290 | 25.7058 | 6494 | 225 | 6719 | 0.045051 | 0.35816 | 6267.7689 | 4.4673 | 893.469 | 7161.2378 | 141 | 7302.2378 | -667.2378 | 10.27%
1400 | 1422 | 1400.1231 | 10.9385 |  | 130 | API Grade X42 | 290 | 27.7141 | 6851 | 225 | 7076 | 0.04849 | 0.3855 | 6746.1695 | 4.4673 | 893.469 | 7639.6384 | 142 | 7781.6384 | -788.6384 | 11.51%
1400 | 1422 | 1398.3 | 11.85 |  | 120 | API Grade X42 | 290 | 30.0627 | 7377 | 225 | 7602 | 0.052497 | 0.41735 | 7303.6291 | 4.4673 | 893.469 | 8197.0981 | 143 | 8340.0981 | -820.0981 | 11.12%
1400 | 1422 | 1396.1455 | 12.9273 |  | 110 | API Grade X42 | 290 | 32.8463 | 7935 | 225 | 8160 | 0.057226 | 0.45494 | 7961.5086 | 4.4673 | 893.469 | 8854.9776 | 144 | 8998.9776 | -919.9776 | 11.59%
1400 | 1422 | 1393.56 | 14.22 |  | 100 | API Grade X42 | 290 | 36.198 | 8655 | 225 | 8880 | 0.06289 | 0.49998 | 8749.6249 | 4.4673 | 893.469 | 9643.0939 | 145 | 9788.0939 | -988.0939 | 11.42%
1500 | 1524 | 1504.95 | 9.525 |  | 160 | API Grade X42 | 290 | 22.4519 | 6607 | 225 | 6832 | 0.045319 | 0.36028 | 6304.9572 | 4.7878 | 957.5574 | 7262.5146 | 146 | 7408.5146 | -655.5146 | 9.922%
1500 | 1524 | 1503.68 | 10.16 |  | 150 | API Grade X42 | 290 | 23.9689 | 6984 | 225 | 7209 | 0.04832 | 0.38414 | 6722.4679 | 4.7878 | 957.5574 | 7680.0253 | 147 | 7827.0253 | -696.0253 | 9.966%
1500 | 1524 | 1502.2286 | 10.8857 |  | 140 | API Grade X42 | 290 | 25.7058 | 7440 | 225 | 7665 | 0.051746 | 0.41138 | 7199.1913 | 4.7878 | 957.5574 | 8156.7487 | 148 | 8304.7487 | -716.7487 | 9.634%
1500 | 1524 | 1500.5538 | 11.7231 |  | 130 | API Grade X42 | 290 | 27.7141 | 7880 | 225 | 8105 | 0.055696 | 0.44278 | 7748.6847 | 4.7878 | 957.5574 | 8706.2421 | 149 | 8855.2421 | -826.2421 | 10.49%
1500 | 1524 | 1498.6 | 12.7 |  | 120 | API Grade X42 | 290 | 30.0627 | 8406 | 225 | 8631 | 0.060298 | 0.47937 | 8388.9857 | 4.7878 | 957.5574 | 9346.5431 | 150 | 9496.5431 | -940.5431 | 11.19%
1500 | 1524 | 1496.2909 | 13.8545 |  | 110 | API Grade X42 | 290 | 32.8463 | 9186 | 225 | 9411 | 0.06573 | 0.52255 | 9144.6294 | 4.7878 | 957.5574 | 10102.1869 | 151 | 10253.1869 | -916.1869 | 9.974%
1500 | 1524 | 1493.52 | 15.24 |  | 100 | API Grade X42 | 290 | 36.198 | 10095 | 225 | 10320 | 0.072236 | 0.57428 | 10049.8639 | 4.7878 | 957.5574 | 11007.4213 | 152 | 11159.4213 | -912.4213 | 9.038%
1600 | 1626 | 1605.675 | 10.1625 |  | 160 | API Grade X42 | 290 | 22.4519 | 7455 | 350 | 7805 | 0.051588 | 0.41012 | 7177.171 | 5.1082 | 1021.6459 | 8198.8169 | 153 | 8351.8169 | -743.8169 | 9.977%
1600 | 1626 | 1604.32 | 10.84 |  | 150 | API Grade X42 | 290 | 23.9689 | 7846 | 350 | 8196 | 0.055004 | 0.43728 | 7652.4391 | 5.1082 | 1021.6459 | 8674.085 | 154 | 8828.085 | -828.085 | 10.55%
1600 | 1626 | 1602.7714 | 11.6143 |  | 140 | API Grade X42 | 290 | 25.7058 | 8363 | 350 | 8713 | 0.058905 | 0.46829 | 8195.1114 | 5.1082 | 1021.6459 | 9216.7573 | 155 | 9371.7573 | -853.7573 | 10.21%
1600 | 1626 | 1600.9846 | 12.5077 |  | 130 | API Grade X42 | 290 | 27.7141 | 8885 | 350 | 9235 | 0.063401 | 0.50404 | 8820.6205 | 5.1082 | 1021.6459 | 9842.2664 | 156 | 9998.2664 | -957.2664 | 10.77%
1600 | 1626 | 1598.9 | 13.55 |  | 120 | API Grade X42 | 290 | 30.0627 | 9588 | 350 | 9938 | 0.06864 | 0.54569 | 9549.4993 | 5.1082 | 1021.6459 | 10571.1452 | 157 | 10728.1452 | -983.1452 | 10.25%
1600 | 1626 | 1596.4364 | 14.7818 |  | 110 | API Grade X42 | 290 | 32.8463 | 10341 | 350 | 10691 | 0.074822 | 0.59484 | 10409.6771 | 5.1082 | 1021.6459 | 11431.3231 | 158 | 11589.3231 | -1090.3231 | 10.54%
1600 | 1626 | 1593.48 | 16.26 |  | 100 | API Grade X42 | 290 | 36.198 | 11320 | 350 | 11670 | 0.082229 | 0.65372 | 11440.1397 | 5.1082 | 1021.6459 | 12461.7856 | 159 | 12620.7856 | -1141.7856 | 10.09%
1700 | 1727 | 1705.4125 | 10.7937 |  | 160 | API Grade X42 | 290 | 22.4519 | 8300 | 350 | 8650 | 0.058196 | 0.46266 | 8096.4919 | 5.4255 | 1085.1061 | 9181.598 | 160 | 9341.598 | -881.598 | 10.62%
1700 | 1727 | 1703.9733 | 11.5133 |  | 150 | API Grade X42 | 290 | 23.9689 | 8746 | 350 | 9096 | 0.06205 | 0.49329 | 8632.6369 | 5.4255 | 1085.1061 | 9717.743 | 161 | 9878.743 | -971.743 | 11.11%
1700 | 1727 | 1702.3286 | 12.3357 |  | 140 | API Grade X42 | 290 | 25.7058 | 9281 | 350 | 9631 | 0.06645 | 0.52828 | 9244.8199 | 5.4255 | 1085.1061 | 10329.926 | 162 | 10491.926 | -1048.926 | 11.3%
1700 | 1727 | 1700.4308 | 13.2846 |  | 130 | API Grade X42 | 290 | 27.7141 | 9914 | 350 | 10264 | 0.071522 | 0.5686 | 9950.4502 | 5.4255 | 1085.1061 | 11035.5563 | 163 | 11198.5563 | -1121.5563 | 11.31%
1700 | 1727 | 1698.2167 | 14.3917 |  | 120 | API Grade X42 | 290 | 30.0627 | 10701 | 350 | 11051 | 0.077432 | 0.61558 | 10772.6908 | 5.4255 | 1085.1061 | 11857.7969 | 164 | 12021.7969 | -1156.7969 | 10.81%
1700 | 1727 | 1695.6 | 15.7 |  | 110 | API Grade X42 | 290 | 32.8463 | 11615 | 350 | 11965 | 0.084406 | 0.67103 | 11743.0485 | 5.4255 | 1085.1061 | 12828.1546 | 165 | 12993.1546 | -1213.1546 | 10.44%
1700 | 1727 | 1692.46 | 17.27 |  | 100 | API Grade X42 | 290 | 36.198 | 12771 | 350 | 13121 | 0.092762 | 0.73746 | 12905.5025 | 5.4255 | 1085.1061 | 13990.6086 | 166 | 14156.6086 | -1219.6086 | 9.55%
1800 | 1829 | 1806.1375 | 11.4313 |  | 160 | API Grade X42 | 290 | 22.4519 | 9166 | 700 | 9866 | 0.065273 | 0.51892 | 9081.1243 | 5.746 | 1149.1946 | 10230.3189 | 167 | 10397.3189 | -1064.3189 | 11.61%
1800 | 1829 | 1804.6133 | 12.1933 |  | 150 | API Grade X42 | 290 | 23.9689 | 9731 | 700 | 10431 | 0.069595 | 0.55328 | 9682.4711 | 5.746 | 1149.1946 | 10831.6657 | 168 | 10999.6657 | -1100.6657 | 11.31%
1800 | 1829 | 1802.8714 | 13.0643 |  | 140 | API Grade X42 | 290 | 25.7058 | 10337 | 700 | 11037 | 0.074531 | 0.59252 | 10369.103 | 5.746 | 1149.1946 | 11518.2976 | 169 | 11687.2976 | -1181.2976 | 11.43%
1800 | 1829 | 1800.8615 | 14.0692 |  | 130 | API Grade X42 | 290 | 27.7141 | 11101 | 700 | 11801 | 0.08022 | 0.63775 | 11160.5466 | 5.746 | 1149.1946 | 12309.7412 | 170 | 12479.7412 | -1208.7412 | 10.89%
1800 | 1829 | 1798.5167 | 15.2417 |  | 120 | API Grade X42 | 290 | 30.0627 | 11857 | 700 | 12557 | 0.086848 | 0.69044 | 12082.7817 | 5.746 | 1149.1946 | 13231.9763 | 171 | 13402.9763 | -1374.9763 | 11.6%
1800 | 1829 | 1795.7455 | 16.6273 |  | 110 | API Grade X42 | 290 | 32.8463 | 12907 | 700 | 13607 | 0.094671 | 0.75264 | 13171.1468 | 5.746 | 1149.1946 | 14320.3413 | 172 | 14492.3413 | -1413.3413 | 10.95%
1800 | 1829 | 1792.42 | 18.29 |  | 100 | API Grade X42 | 290 | 36.198 | 14232 | 700 | 14932 | 0.10404 | 0.82714 | 14474.9694 | 5.746 | 1149.1946 | 15624.164 | 173 | 15797.164 | -1392.164 | 9.782%
1900 | 1930 | 1905.875 | 12.0625 |  | 160 | API Grade X42 | 290 | 22.4519 | 10222 | 700 | 10922 | 0.072681 | 0.57781 | 10111.7617 | 6.0633 | 1212.6548 | 11324.4165 | 174 | 11498.4165 | -1102.4165 | 10.78%
1900 | 1930 | 1904.2667 | 12.8667 |  | 150 | API Grade X42 | 290 | 23.9689 | 10881 | 700 | 11581 | 0.077494 | 0.61608 | 10781.3568 | 6.0633 | 1212.6548 | 11994.0116 | 175 | 12169.0116 | -1113.0116 | 10.23%
1900 | 1930 | 1902.4286 | 13.7857 |  | 140 | API Grade X42 | 290 | 25.7058 | 11590 | 700 | 12290 | 0.08299 | 0.65977 | 11545.9161 | 6.0633 | 1212.6548 | 12758.5709 | 176 | 12934.5709 | -1168.5709 | 10.08%
1900 | 1930 | 1900.3077 | 14.8462 |  | 130 | API Grade X42 | 290 | 27.7141 | 12027 | 700 | 12727 | 0.089324 | 0.71012 | 12427.1824 | 6.0633 | 1212.6548 | 13639.8372 | 177 | 13816.8372 | -1612.8372 | 13.41%
1900 | 1930 | 1897.8333 | 16.0833 |  | 120 | API Grade X42 | 290 | 30.0627 | 13238 | 700 | 13938 | 0.096705 | 0.7688 | 13454.0841 | 6.0633 | 1212.6548 | 14666.7388 | 178 | 14844.7388 | -1428.7388 | 10.79%
1900 | 1930 | 1894.9091 | 17.5455 |  | 110 | API Grade X42 | 290 | 32.8463 | 14277 | 700 | 14977 | 0.10542 | 0.83806 | 14665.9701 | 6.0633 | 1212.6548 | 15878.6249 | 179 | 16057.6249 | -1601.6249 | 11.22%
1900 | 1930 | 1891.4 | 19.3 |  | 100 | API Grade X42 | 290 | 36.198 | 15608 | 700 | 16308 | 0.11585 | 0.92102 | 16117.7666 | 6.0633 | 1212.6548 | 17330.4214 | 180 | 17510.4214 | -1722.4214 | 11.04%
2000 | 2032 | 2006.6 | 12.7 |  | 160 | API Grade X42 | 290 | 22.4519 | 11159 | 700 | 11859 | 0.080566 | 0.6405 | 11208.8128 | 6.3837 | 1276.7433 | 12485.5561 | 181 | 12666.5561 | -1326.5561 | 11.89%
2000 | 2032 | 2004.9067 | 13.5467 |  | 150 | API Grade X42 | 290 | 23.9689 | 11798 | 700 | 12498 | 0.085902 | 0.68292 | 11951.054 | 6.3837 | 1276.7433 | 13227.7972 | 182 | 13409.7972 | -1429.7972 | 12.12%
2000 | 2032 | 2002.9714 | 14.5143 |  | 140 | API Grade X42 | 290 | 25.7058 | 12677 | 700 | 13377 | 0.091993 | 0.73135 | 12798.5623 | 6.3837 | 1276.7433 | 14075.3055 | 183 | 14258.3055 | -1398.3055 | 11.03%
2000 | 2032 | 2000.7385 | 15.6308 |  | 130 | API Grade X42 | 290 | 27.7141 | 13538 | 700 | 14238 | 0.099015 | 0.78717 | 13775.4395 | 6.3837 | 1276.7433 | 15052.1827 | 184 | 15236.1827 | -1514.1827 | 11.18%
2000 | 2032 | 1998.1333 | 16.9333 |  | 120 | API Grade X42 | 290 | 30.0627 | 14441 | 700 | 15141 | 0.1072 | 0.85221 | 14913.7523 | 6.3837 | 1276.7433 | 16190.4956 | 185 | 16375.4956 | -1749.4956 | 12.11%
2000 | 2032 | 1995.0545 | 18.4727 |  | 110 | API Grade X42 | 290 | 32.8463 | 15816 | 700 | 16516 | 0.11685 | 0.92898 | 16257.119 | 6.3837 | 1276.7433 | 17533.8623 | 186 | 17719.8623 | -1717.8623 | 10.86%
2000 | 2032 | 1991.36 | 20.32 |  | 100 | API Grade X42 | 290 | 36.198 | 17251 | 700 | 17951 | 0.12842 | 1.0209 | 17866.4246 | 6.3837 | 1276.7433 | 19143.1679 | 187 | 19330.1679 | -1892.1679 | 10.97%
2100 | 2134 | 2107.325 | 13.3375 |  | 160 | API Grade X42 | 290 | 22.4519 | 12275 | 700 | 12975 | 0.088858 | 0.70642 | 12362.3501 | 6.7042 | 1340.8317 | 13703.1819 | 188 | 13891.1819 | -1428.1819 | 11.63%
2100 | 2134 | 2105.5467 | 14.2267 |  | 150 | API Grade X42 | 290 | 23.9689 | 13145 | 700 | 13845 | 0.094742 | 0.7532 | 13180.9779 | 6.7042 | 1340.8317 | 14521.8096 | 189 | 14710.8096 | -1376.8096 | 10.47%
2100 | 2134 | 2103.5143 | 15.2429 |  | 140 | API Grade X42 | 290 | 25.7058 | 13995 | 700 | 14695 | 0.10146 | 0.80661 | 14115.7062 | 6.7042 | 1340.8317 | 15456.5379 | 190 | 15646.5379 | -1461.5379 | 10.44%
2100 | 2134 | 2101.1692 | 16.4154 |  | 130 | API Grade X42 | 290 | 27.7141 | 14809 | 700 | 15509 | 0.1092 | 0.86818 | 15193.1171 | 6.7042 | 1340.8317 | 16533.9489 | 191 | 16724.9489 | -1724.9489 | 11.65%
2100 | 2134 | 2098.4333 | 17.7833 |  | 120 | API Grade X42 | 290 | 30.0627 | 16039 | 700 | 16739 | 0.11823 | 0.93992 | 16448.5777 | 6.7042 | 1340.8317 | 17789.4094 | 192 | 17981.4094 | -1750.4094 | 10.91%
2100 | 2134 | 2095.2 | 19.4 |  | 110 | API Grade X42 | 290 | 32.8463 | 17293 | 700 | 17993 | 0.12888 | 1.0246 | 17930.1948 | 6.7042 | 1340.8317 | 19271.0265 | 193 | 19464.0265 | -1978.0265 | 11.44%
2100 | 2134 | 2091.32 | 21.34 |  | 100 | API Grade X42 | 290 | 36.198 | 18775 | 700 | 19475 | 0.14164 | 1.126 | 19705.1196 | 6.7042 | 1340.8317 | 21045.9513 | 194 | 21239.9513 | -2270.9513 | 12.1%
2200 | 2236 | 2208.05 | 13.975 |  | 160 | API Grade X42 | 290 | 22.4519 | 13803 | 700 | 14503 | 0.097555 | 0.77556 | 13572.3737 | 7.0246 | 1404.9202 | 14977.2939 | 195 | 15172.2939 | -1174.2939 | 8.508%
2200 | 2236 | 2206.1867 | 14.9067 |  | 150 | API Grade X42 | 290 | 23.9689 | 14611 | 700 | 15311 | 0.10402 | 0.82692 | 14471.1285 | 7.0246 | 1404.9202 | 15876.0487 | 196 | 16072.0487 | -1265.0487 | 8.658%
2200 | 2236 | 2204.0571 | 15.9714 |  | 140 | API Grade X42 | 290 | 25.7058 | 15600 | 700 | 16300 | 0.11139 | 0.88556 | 15497.3477 | 7.0246 | 1404.9202 | 16902.2679 | 197 | 17099.2679 | -1302.2679 | 8.348%
2200 | 2236 | 2201.6 | 17.2 |  | 130 | API Grade X42 | 290 | 27.7141 | 16784 | 700 | 17484 | 0.11989 | 0.95316 | 16680.2154 | 7.0246 | 1404.9202 | 18085.1356 | 198 | 18283.1356 | -1301.1356 | 7.752%
2200 | 2236 | 2198.7333 | 18.6333 |  | 120 | API Grade X42 | 290 | 30.0627 | 17741 | 700 | 18441 | 0.1298 | 1.0319 | 18058.5601 | 7.0246 | 1404.9202 | 19463.4803 | 199 | 19662.4803 | -1722.4803 | 9.709%
2200 | 2236 | 2195.3455 | 20.3273 |  | 110 | API Grade X42 | 290 | 32.8463 | 19479 | 700 | 20179 | 0.14149 | 1.1249 | 19685.1975 | 7.0246 | 1404.9202 | 21090.1177 | 200 | 21290.1177 | -1611.1177 | 8.271%
2300 | 2337 | 2307.7875 | 14.6062 |  | 160 | API Grade X42 | 290 | 22.4519 | 14880 | 700 | 15580 | 0.10657 | 0.84721 | 14826.1925 | 7.3419 | 1468.3804 | 16294.5729 | 201 | 16495.5729 | -1414.5729 | 9.507%
2300 | 2337 | 2305.84 | 15.58 |  | 150 | API Grade X42 | 290 | 23.9689 | 15777 | 700 | 16477 | 0.11362 | 0.90331 | 15807.9744 | 7.3419 | 1468.3804 | 17276.3548 | 202 | 17478.3548 | -1499.3548 | 9.503%
2300 | 2337 | 2303.6143 | 16.6929 |  | 140 | API Grade X42 | 290 | 25.7058 | 16759 | 700 | 17459 | 0.12168 | 0.96737 | 16928.9961 | 7.3419 | 1468.3804 | 18397.3765 | 203 | 18600.3765 | -1638.3765 | 9.776%
2300 | 2337 | 2301.0462 | 17.9769 |  | 130 | API Grade X42 | 290 | 27.7141 | 17915 | 700 | 18615 | 0.13097 | 1.0412 | 18221.1373 | 7.3419 | 1468.3804 | 19689.5177 | 204 | 19893.5177 | -1774.5177 | 9.905%
2300 | 2337 | 2298.05 | 19.475 |  | 120 | API Grade X42 | 290 | 30.0627 | 19249 | 700 | 19949 | 0.14179 | 1.1272 | 19726.8137 | 7.3419 | 1468.3804 | 21195.1942 | 205 | 21400.1942 | -1946.1942 | 10.11%
2300 | 2337 | 2294.5091 | 21.2455 |  | 110 | API Grade X42 | 290 | 32.8463 | 20765 | 700 | 21465 | 0.15456 | 1.2288 | 21503.7203 | 7.3419 | 1468.3804 | 22972.1007 | 206 | 23178.1007 | -2207.1007 | 10.63%
2400 | 2450 | 2419.375 | 15.3125 |  | 160 | API Grade X42 | 290 | 22.4519 | 16224 | 700 | 16924 | 0.11712 | 0.93112 | 16294.6253 | 7.6969 | 1539.3804 | 17834.0057 | 207 | 18041.0057 | -1610.0057 | 9.924%
2400 | 2450 | 2417.3333 | 16.3333 |  | 150 | API Grade X42 | 290 | 23.9689 | 17165 | 700 | 17865 | 0.12488 | 0.99278 | 17373.646 | 7.6969 | 1539.3804 | 18913.0264 | 208 | 19121.0264 | -1748.0264 | 10.18%
2400 | 2450 | 2415 | 17.5 |  | 140 | API Grade X42 | 290 | 25.7058 | 18288 | 700 | 18988 | 0.13373 | 1.0632 | 18605.6972 | 7.6969 | 1539.3804 | 20145.0776 | 209 | 20354.0776 | -1857.0776 | 10.15%
2400 | 2450 | 2412.3077 | 18.8462 |  | 130 | API Grade X42 | 290 | 27.7141 | 19867 | 700 | 20567 | 0.14394 | 1.1443 | 20025.8161 | 7.6969 | 1539.3804 | 21565.1965 | 210 | 21775.1965 | -1698.1965 | 8.548%
2400 | 2450 | 2409.1667 | 20.4167 |  | 120 | API Grade X42 | 290 | 30.0627 | 21014 | 700 | 21714 | 0.15584 | 1.2389 | 21680.6195 | 7.6969 | 1539.3804 | 23219.9999 | 211 | 23430.9999 | -2205.9999 | 10.5%
2500 | 2540 | 2508.25 | 15.875 |  | 160 | API Grade X42 | 290 | 22.4519 | 17395 | 700 | 18095 | 0.12589 | 1.0008 | 17513.77 | 7.9796 | 1595.9291 | 19109.6991 | 212 | 19321.6991 | -1714.6991 | 9.857%
2500 | 2540 | 2506.1333 | 16.9333 |  | 150 | API Grade X42 | 290 | 23.9689 | 18382 | 700 | 19082 | 0.13422 | 1.0671 | 18673.5218 | 7.9796 | 1595.9291 | 20269.4509 | 213 | 20482.4509 | -1887.4509 | 10.27%
2500 | 2540 | 2503.7143 | 18.1429 |  | 140 | API Grade X42 | 290 | 25.7058 | 19562 | 700 | 20262 | 0.14374 | 1.1427 | 19997.7536 | 7.9796 | 1595.9291 | 21593.6826 | 214 | 21807.6826 | -2031.6826 | 10.39%
2500 | 2540 | 2500.9231 | 19.5385 |  | 130 | API Grade X42 | 290 | 27.7141 | 20939 | 700 | 21639 | 0.15471 | 1.2299 | 21524.1242 | 7.9796 | 1595.9291 | 23120.0532 | 215 | 23335.0532 | -2181.0532 | 10.42%
2500 | 2540 | 2497.6667 | 21.1667 |  | 120 | API Grade X42 | 290 | 30.0627 | 22608 | 700 | 23308 | 0.16749 | 1.3316 | 23302.738 | 7.9796 | 1595.9291 | 24898.6671 | 216 | 25114.6671 | -2290.6671 | 10.13%
500 | 508 | 498.7636 | 4.6182 |  | 110 | API Grade X52 | 350 | 39.6421 | 1364.2863 | 85 | 1449.2863 | 0.0073033 | 0.058061 | 1045.1005 | 1.5959 | 319.1858 | 1364.2863 | 85 | 1449.2863 | 0 | 0% |  | 18000
500 | 508 | 497.84 | 5.08 |  | 100 | API Grade X52 | 350 | 43.6872 | 1467.7417 | 85 | 1552.7417 | 0.0080262 | 0.063809 | 1148.5559 | 1.5959 | 319.1858 | 1467.7417 | 85 | 1552.7417 | 0 | 0%
600 | 610 | 601.2857 | 4.3571 |  | 140 | API Grade X52 | 350 | 31.0242 | 1569.6108 | 85 | 1654.6108 | 0.0082903 | 0.065908 | 1186.3365 | 1.9164 | 383.2743 | 1569.6108 | 85 | 1654.6108 | 0 | 0%
600 | 610 | 600.6154 | 4.6923 |  | 130 | API Grade X52 | 350 | 33.448 | 1660.1605 | 85 | 1745.1605 | 0.008923 | 0.070938 | 1276.8862 | 1.9164 | 383.2743 | 1660.1605 | 85 | 1745.1605 | 0 | 0%
600 | 610 | 599.8333 | 5.0833 |  | 120 | API Grade X52 | 350 | 36.2826 | 1765.6741 | 85 | 1850.6741 | 0.0096604 | 0.0768 | 1382.3997 | 1.9164 | 383.2743 | 1765.6741 | 85 | 1850.6741 | 0 | 0%
600 | 610 | 598.9091 | 5.5455 |  | 110 | API Grade X52 | 350 | 39.6421 | 1890.1947 | 85 | 1975.1947 | 0.010531 | 0.083718 | 1506.9204 | 1.9164 | 383.2743 | 1890.1947 | 85 | 1975.1947 | 0 | 0%
600 | 610 | 597.8 | 6.1 |  | 100 | API Grade X52 | 350 | 43.6872 | 2039.366 | 85 | 2124.366 | 0.011573 | 0.092005 | 1656.0917 | 1.9164 | 383.2743 | 2039.366 | 85 | 2124.366 | 0 | 0%
700 | 711 | 700.8429 | 5.0786 |  | 140 | API Grade X52 | 350 | 31.0242 | 2069 | 85 | 2154 | 0.011263 | 0.08954 | 1611.712 | 2.2337 | 446.7345 | 2058.4465 | 212 | 2270.4465 | 10.5535 | -0.5101%
700 | 711 | 700.0615 | 5.4692 |  | 130 | API Grade X52 | 350 | 33.448 | 2137 | 85 | 2222 | 0.012122 | 0.096374 | 1734.7293 | 2.2337 | 446.7345 | 2181.4638 | 212 | 2393.4638 | -44.4638 | 2.081%
700 | 711 | 699.15 | 5.925 |  | 120 | API Grade X52 | 350 | 36.2826 | 2235 | 85 | 2320 | 0.013124 | 0.10434 | 1878.0761 | 2.2337 | 446.7345 | 2324.8105 | 212 | 2536.8105 | -89.8105 | 4.018%
700 | 711 | 698.0727 | 6.4636 |  | 110 | API Grade X52 | 350 | 39.6421 | 2381 | 85 | 2466 | 0.014306 | 0.11374 | 2047.2451 | 2.2337 | 446.7345 | 2493.9796 | 212 | 2705.9796 | -112.9796 | 4.745%
700 | 711 | 696.78 | 7.11 |  | 100 | API Grade X52 | 350 | 43.6872 | 2537 | 85 | 2622 | 0.015723 | 0.12499 | 2249.9036 | 2.2337 | 446.7345 | 2696.638 | 212 | 2908.638 | -159.638 | 6.292%
800 | 813 | 802.8375 | 5.0812 |  | 160 | API Grade X52 | 350 | 27.0971 | 2320 | 110 | 2430 | 0.012897 | 0.10253 | 1845.5582 | 2.5541 | 510.823 | 2356.3812 | 212 | 2568.3812 | -36.3812 | 1.568%
800 | 813 | 802.16 | 5.42 |  | 150 | API Grade X52 | 350 | 28.928 | 2404 | 110 | 2514 | 0.013751 | 0.10932 | 1967.7701 | 2.5541 | 510.823 | 2478.593 | 212 | 2690.593 | -74.593 | 3.103%
800 | 813 | 801.3857 | 5.8071 |  | 140 | API Grade X52 | 350 | 31.0242 | 2516 | 110 | 2626 | 0.014726 | 0.11707 | 2107.3144 | 2.5541 | 510.823 | 2618.1373 | 212 | 2830.1373 | -102.1373 | 4.06%
800 | 813 | 800.4923 | 6.2538 |  | 130 | API Grade X52 | 350 | 33.448 | 2656 | 110 | 2766 | 0.01585 | 0.12601 | 2268.1596 | 2.5541 | 510.823 | 2778.9825 | 212 | 2990.9825 | -122.9825 | 4.63%
800 | 813 | 799.45 | 6.775 |  | 120 | API Grade X52 | 350 | 36.2826 | 2796 | 110 | 2906 | 0.01716 | 0.13642 | 2455.5855 | 2.5541 | 510.823 | 2966.4085 | 212 | 3178.4085 | -170.4085 | 6.095%
800 | 813 | 798.2182 | 7.3909 |  | 110 | API Grade X52 | 350 | 39.6421 | 2964 | 110 | 3074 | 0.018706 | 0.14871 | 2676.7741 | 2.5541 | 510.823 | 3187.5971 | 212 | 3399.5971 | -223.5971 | 7.544%
800 | 813 | 796.74 | 8.13 |  | 100 | API Grade X52 | 350 | 43.6872 | 3162 | 110 | 3272 | 0.020557 | 0.16343 | 2941.7502 | 2.5541 | 510.823 | 3452.5732 | 212 | 3664.5732 | -290.5732 | 9.19%
900 | 914 | 902.575 | 5.7125 |  | 160 | API Grade X52 | 350 | 27.0971 | 2779 | 135 | 2914 | 0.0163 | 0.12959 | 2332.5935 | 2.8714 | 574.2831 | 2906.8766 | 212 | 3118.8766 | -127.8766 | 4.602%
900 | 914 | 901.8133 | 6.0933 |  | 150 | API Grade X52 | 350 | 28.928 | 2906 | 135 | 3041 | 0.01738 | 0.13817 | 2487.0565 | 2.8714 | 574.2831 | 3061.3396 | 212 | 3273.3396 | -155.3396 | 5.345%
900 | 914 | 900.9429 | 6.5286 |  | 140 | API Grade X52 | 350 | 31.0242 | 3032 | 135 | 3167 | 0.018612 | 0.14797 | 2663.426 | 2.8714 | 574.2831 | 3237.7091 | 212 | 3449.7091 | -205.7091 | 6.785%
900 | 914 | 899.9385 | 7.0308 |  | 130 | API Grade X52 | 350 | 33.448 | 3190 | 135 | 3325 | 0.020033 | 0.15926 | 2866.7175 | 2.8714 | 574.2831 | 3441.0007 | 212 | 3653.0007 | -251.0007 | 7.868%
900 | 914 | 898.7667 | 7.6167 |  | 120 | API Grade X52 | 350 | 36.2826 | 3387 | 135 | 3522 | 0.021688 | 0.17242 | 3103.6045 | 2.8714 | 574.2831 | 3677.8876 | 212 | 3889.8876 | -290.8876 | 8.588%
900 | 914 | 897.3818 | 8.3091 |  | 110 | API Grade X52 | 350 | 39.6421 | 3610 | 135 | 3745 | 0.023642 | 0.18795 | 3383.1638 | 2.8714 | 574.2831 | 3957.4469 | 212 | 4169.4469 | -347.4469 | 9.625%
900 | 914 | 895.72 | 9.14 |  | 100 | API Grade X52 | 350 | 43.6872 | 3861 | 135 | 3996 | 0.025982 | 0.20656 | 3718.066 | 2.8714 | 574.2831 | 4292.3491 | 212 | 4504.3491 | -431.3491 | 11.17%
1000 | 1016 | 1003.3 | 6.35 |  | 160 | API Grade X52 | 350 | 27.0971 | 3363 | 170 | 3533 | 0.020142 | 0.16013 | 2882.2662 | 3.1919 | 638.3716 | 3520.6378 | 212 | 3732.6378 | -157.6378 | 4.687%
1000 | 1016 | 1002.4533 | 6.7733 |  | 150 | API Grade X52 | 350 | 28.928 | 3505 | 170 | 3675 | 0.021475 | 0.17073 | 3073.1282 | 3.1919 | 638.3716 | 3711.4998 | 212 | 3923.4998 | -206.4998 | 5.892%
1000 | 1016 | 1001.4857 | 7.2571 |  | 140 | API Grade X52 | 350 | 31.0242 | 3680 | 170 | 3850 | 0.022998 | 0.18284 | 3291.0589 | 3.1919 | 638.3716 | 3929.4305 | 212 | 4141.4305 | -249.4305 | 6.778%
1000 | 1016 | 1000.3692 | 7.8154 |  | 130 | API Grade X52 | 350 | 33.448 | 3856 | 170 | 4026 | 0.024754 | 0.19679 | 3542.2559 | 3.1919 | 638.3716 | 4180.6275 | 212 | 4392.6275 | -324.6275 | 8.419%
1000 | 1016 | 999.0667 | 8.4667 |  | 120 | API Grade X52 | 350 | 36.2826 | 4105 | 170 | 4275 | 0.026799 | 0.21305 | 3834.9649 | 3.1919 | 638.3716 | 4473.3365 | 212 | 4685.3365 | -368.3365 | 8.973%
1000 | 1016 | 997.5273 | 9.2364 |  | 110 | API Grade X52 | 350 | 39.6421 | 4371 | 170 | 4541 | 0.029213 | 0.23224 | 4180.402 | 3.1919 | 638.3716 | 4818.7737 | 212 | 5030.7737 | -447.7737 | 10.24%
1000 | 1016 | 995.68 | 10.16 |  | 100 | API Grade X52 | 350 | 43.6872 | 4728 | 170 | 4898 | 0.032105 | 0.25523 | 4594.2235 | 3.1919 | 638.3716 | 5232.5951 | 212 | 5444.5951 | -504.5951 | 10.67%
1100 | 1118 | 1104.025 | 6.9875 |  | 160 | API Grade X52 | 350 | 27.0971 | 3925 | 225 | 4150 | 0.024389 | 0.19389 | 3490.0389 | 3.5123 | 702.4601 | 4192.4991 | 212 | 4404.4991 | -267.4991 | 6.815%
1100 | 1118 | 1103.0933 | 7.4533 |  | 150 | API Grade X52 | 350 | 28.928 | 4118 | 225 | 4343 | 0.026004 | 0.20673 | 3721.1473 | 3.5123 | 702.4601 | 4423.6074 | 212 | 4635.6074 | -305.6074 | 7.421%
1100 | 1118 | 1102.0286 | 7.9857 |  | 140 | API Grade X52 | 350 | 31.0242 | 4316 | 225 | 4541 | 0.027848 | 0.22139 | 3985.0323 | 3.5123 | 702.4601 | 4687.4924 | 212 | 4899.4924 | -371.4924 | 8.607%
1100 | 1118 | 1100.8 | 8.6 |  | 130 | API Grade X52 | 350 | 33.448 | 4548 | 225 | 4773 | 0.029973 | 0.23829 | 4289.1982 | 3.5123 | 702.4601 | 4991.6584 | 212 | 5203.6584 | -443.6584 | 9.755%
1100 | 1118 | 1099.3667 | 9.3167 |  | 120 | API Grade X52 | 350 | 36.2826 | 4830 | 225 | 5055 | 0.03245 | 0.25798 | 4643.6297 | 3.5123 | 702.4601 | 5346.0898 | 212 | 5558.0898 | -516.0898 | 10.69%
1100 | 1118 | 1097.6727 | 10.1636 |  | 110 | API Grade X52 | 350 | 39.6421 | 5185 | 225 | 5410 | 0.035373 | 0.28122 | 5061.9079 | 3.5123 | 702.4601 | 5764.368 | 212 | 5976.368 | -579.368 | 11.17%
1100 | 1118 | 1095.64 | 11.18 |  | 100 | API Grade X52 | 350 | 43.6872 | 5570 | 225 | 5795 | 0.038875 | 0.30906 | 5562.9904 | 3.5123 | 702.4601 | 6265.4505 | 212 | 6477.4505 | -695.4505 | 12.49%
1200 | 1219 | 1203.7625 | 7.6188 |  | 160 | API Grade X52 | 350 | 27.0971 | 4515 | 225 | 4740 | 0.028994 | 0.23051 | 4149.1017 | 3.8296 | 765.9203 | 4915.022 | 212 | 5127.022 | -400.022 | 8.86%
1200 | 1219 | 1202.7467 | 8.1267 |  | 150 | API Grade X52 | 350 | 28.928 | 4730 | 225 | 4955 | 0.030914 | 0.24577 | 4423.8528 | 3.8296 | 765.9203 | 5189.7731 | 212 | 5401.7731 | -459.7731 | 9.72%
1200 | 1219 | 1201.5857 | 8.7071 |  | 140 | API Grade X52 | 350 | 31.0242 | 4984 | 225 | 5209 | 0.033107 | 0.2632 | 4737.5701 | 3.8296 | 765.9203 | 5503.4904 | 212 | 5715.4904 | -519.4904 | 10.42%
1200 | 1219 | 1200.2462 | 9.3769 |  | 130 | API Grade X52 | 350 | 33.448 | 5318 | 225 | 5543 | 0.035634 | 0.28329 | 5099.1751 | 3.8296 | 765.9203 | 5865.0954 | 212 | 6077.0954 | -547.0954 | 10.29%
1200 | 1219 | 1198.6833 | 10.1583 |  | 120 | API Grade X52 | 350 | 36.2826 | 5663 | 225 | 5888 | 0.038578 | 0.3067 | 5520.5378 | 3.8296 | 765.9203 | 6286.4581 | 212 | 6498.4581 | -623.4581 | 11.01%
1200 | 1219 | 1196.8364 | 11.0818 |  | 110 | API Grade X52 | 350 | 39.6421 | 6155 | 225 | 6380 | 0.042053 | 0.33432 | 6017.8041 | 3.8296 | 765.9203 | 6783.7244 | 212 | 6995.7244 | -628.7244 | 10.21%
1200 | 1219 | 1194.62 | 12.19 |  | 100 | API Grade X52 | 350 | 43.6872 | 6637 | 225 | 6862 | 0.046216 | 0.36742 | 6613.5115 | 3.8296 | 765.9203 | 7379.4318 | 212 | 7591.4318 | -742.4318 | 11.19%
1300 | 1321 | 1304.4875 | 8.2562 |  | 160 | API Grade X52 | 350 | 27.0971 | 5215 | 225 | 5440 | 0.03405 | 0.27069 | 4872.5051 | 4.15 | 830.0088 | 5702.5139 | 212 | 5914.5139 | -487.5139 | 9.348%
1300 | 1321 | 1303.3867 | 8.8067 |  | 150 | API Grade X52 | 350 | 28.928 | 5474 | 225 | 5699 | 0.036304 | 0.28862 | 5195.1596 | 4.15 | 830.0088 | 6025.1684 | 212 | 6237.1684 | -551.1684 | 10.07%
1300 | 1321 | 1302.1286 | 9.4357 |  | 140 | API Grade X52 | 350 | 31.0242 | 5782 | 225 | 6007 | 0.038879 | 0.30909 | 5563.574 | 4.15 | 830.0088 | 6393.5828 | 212 | 6605.5828 | -611.5828 | 10.58%
1300 | 1321 | 1300.6769 | 10.1615 |  | 130 | API Grade X52 | 350 | 33.448 | 6156 | 225 | 6381 | 0.041846 | 0.33268 | 5988.2255 | 4.15 | 830.0088 | 6818.2343 | 212 | 7030.2343 | -662.2343 | 10.76%
1300 | 1321 | 1298.9833 | 11.0083 |  | 120 | API Grade X52 | 350 | 36.2826 | 6522 | 225 | 6747 | 0.045304 | 0.36017 | 6483.0536 | 4.15 | 830.0088 | 7313.0624 | 212 | 7525.0624 | -791.0624 | 12.13%
1300 | 1321 | 1296.9818 | 12.0091 |  | 110 | API Grade X52 | 350 | 39.6421 | 7040 | 225 | 7265 | 0.049385 | 0.39261 | 7067.0192 | 4.15 | 830.0088 | 7897.0279 | 212 | 8109.0279 | -857.0279 | 12.17%
1300 | 1321 | 1294.58 | 13.21 |  | 100 | API Grade X52 | 350 | 43.6872 | 7520 | 225 | 7745 | 0.054274 | 0.43148 | 7766.5892 | 4.15 | 830.0088 | 8596.598 | 212 | 8808.598 | -1076.598 | 14.32%
1400 | 1422 | 1404.225 | 8.8875 |  | 160 | API Grade X52 | 350 | 27.0971 | 5915 | 225 | 6140 | 0.039455 | 0.31367 | 5646.0648 | 4.4673 | 893.469 | 6539.5338 | 212 | 6751.5338 | -624.5338 | 10.56%
1400 | 1422 | 1403.04 | 9.48 |  | 150 | API Grade X52 | 350 | 28.928 | 6225 | 225 | 6450 | 0.042068 | 0.33444 | 6019.944 | 4.4673 | 893.469 | 6913.4129 | 212 | 7125.4129 | -688.4129 | 11.06%
1400 | 1422 | 1401.6857 | 10.1571 |  | 140 | API Grade X52 | 350 | 31.0242 | 6596 | 225 | 6821 | 0.045051 | 0.35816 | 6446.848 | 4.4673 | 893.469 | 7340.3169 | 212 | 7552.3169 | -744.3169 | 11.28%
1400 | 1422 | 1400.1231 | 10.9385 |  | 130 | API Grade X52 | 350 | 33.448 | 6960 | 225 | 7185 | 0.04849 | 0.3855 | 6938.9172 | 4.4673 | 893.469 | 7832.3861 | 212 | 8044.3861 | -872.3861 | 12.53%
1400 | 1422 | 1398.3 | 11.85 |  | 120 | API Grade X52 | 350 | 36.2826 | 7497 | 225 | 7722 | 0.052497 | 0.41735 | 7512.3042 | 4.4673 | 893.469 | 8405.7732 | 212 | 8617.7732 | -908.7732 | 12.12%
1400 | 1422 | 1396.1455 | 12.9273 |  | 110 | API Grade X52 | 350 | 39.6421 | 8065 | 225 | 8290 | 0.057226 | 0.45494 | 8188.9803 | 4.4673 | 893.469 | 9082.4493 | 212 | 9294.4493 | -1017.4493 | 12.62%
1400 | 1422 | 1393.56 | 14.22 |  | 100 | API Grade X52 | 350 | 43.6872 | 8797 | 225 | 9022 | 0.06289 | 0.49998 | 8999.6142 | 4.4673 | 893.469 | 9893.0832 | 212 | 10105.0832 | -1096.0832 | 12.46%
1500 | 1524 | 1504.95 | 9.525 |  | 160 | API Grade X52 | 350 | 27.0971 | 6710 | 225 | 6935 | 0.045319 | 0.36028 | 6485.0988 | 4.7878 | 957.5574 | 7442.6563 | 212 | 7654.6563 | -732.6563 | 10.92%
1500 | 1524 | 1503.68 | 10.16 |  | 150 | API Grade X52 | 350 | 28.928 | 7103 | 225 | 7328 | 0.04832 | 0.38414 | 6914.5384 | 4.7878 | 957.5574 | 7872.0958 | 212 | 8084.0958 | -769.0958 | 10.83%
1500 | 1524 | 1502.2286 | 10.8857 |  | 140 | API Grade X52 | 350 | 31.0242 | 7557 | 225 | 7782 | 0.051746 | 0.41138 | 7404.8825 | 4.7878 | 957.5574 | 8362.4399 | 212 | 8574.4399 | -805.4399 | 10.66%
1500 | 1524 | 1500.5538 | 11.7231 |  | 130 | API Grade X52 | 350 | 33.448 | 7994 | 225 | 8219 | 0.055696 | 0.44278 | 7970.0757 | 4.7878 | 957.5574 | 8927.6331 | 212 | 9139.6331 | -933.6331 | 11.68%
1500 | 1524 | 1498.6 | 12.7 |  | 120 | API Grade X52 | 350 | 36.2826 | 8568 | 225 | 8793 | 0.060298 | 0.47937 | 8628.671 | 4.7878 | 957.5574 | 9586.2284 | 212 | 9798.2284 | -1018.2284 | 11.88%
1500 | 1524 | 1496.2909 | 13.8545 |  | 110 | API Grade X52 | 350 | 39.6421 | 9336 | 225 | 9561 | 0.06573 | 0.52255 | 9405.9046 | 4.7878 | 957.5574 | 10363.462 | 212 | 10575.462 | -1027.462 | 11.01%
1500 | 1524 | 1493.52 | 15.24 |  | 100 | API Grade X52 | 350 | 43.6872 | 10258 | 225 | 10483 | 0.072236 | 0.57428 | 10337.0028 | 4.7878 | 957.5574 | 11294.5603 | 212 | 11506.5603 | -1036.5603 | 10.1%
1600 | 1626 | 1605.675 | 10.1625 |  | 160 | API Grade X52 | 350 | 27.0971 | 7573 | 350 | 7923 | 0.051588 | 0.41012 | 7382.233 | 5.1082 | 1021.6459 | 8403.8789 | 212 | 8615.8789 | -830.8789 | 10.97%
1600 | 1626 | 1604.32 | 10.84 |  | 150 | API Grade X52 | 350 | 28.928 | 7970 | 350 | 8320 | 0.055004 | 0.43728 | 7871.0802 | 5.1082 | 1021.6459 | 8892.7262 | 212 | 9104.7262 | -922.7262 | 11.58%
1600 | 1626 | 1602.7714 | 11.6143 |  | 140 | API Grade X52 | 350 | 31.0242 | 8495 | 350 | 8845 | 0.058905 | 0.46829 | 8429.2574 | 5.1082 | 1021.6459 | 9450.9034 | 212 | 9662.9034 | -955.9034 | 11.25%
1600 | 1626 | 1600.9846 | 12.5077 |  | 130 | API Grade X52 | 350 | 33.448 | 9029 | 350 | 9379 | 0.063401 | 0.50404 | 9072.6382 | 5.1082 | 1021.6459 | 10094.2842 | 212 | 10306.2842 | -1065.2842 | 11.8%
1600 | 1626 | 1598.9 | 13.55 |  | 120 | API Grade X52 | 350 | 36.2826 | 9745 | 350 | 10095 | 0.06864 | 0.54569 | 9822.3422 | 5.1082 | 1021.6459 | 10843.9881 | 212 | 11055.9881 | -1098.9881 | 11.28%
1600 | 1626 | 1596.4364 | 14.7818 |  | 110 | API Grade X52 | 350 | 39.6421 | 10511 | 350 | 10861 | 0.074822 | 0.59484 | 10707.0965 | 5.1082 | 1021.6459 | 11728.7424 | 212 | 11940.7424 | -1217.7424 | 11.59%
1700 | 1727 | 1705.4125 | 10.7937 |  | 160 | API Grade X52 | 350 | 27.0971 | 8432 | 350 | 8782 | 0.058196 | 0.46266 | 8327.8202 | 5.4255 | 1085.1061 | 9412.9263 | 212 | 9624.9263 | -980.9263 | 11.63%
1700 | 1727 | 1703.9733 | 11.5133 |  | 150 | API Grade X52 | 350 | 28.928 | 8886 | 350 | 9236 | 0.06205 | 0.49329 | 8879.2837 | 5.4255 | 1085.1061 | 9964.3898 | 212 | 10176.3898 | -1078.3898 | 12.14%
1700 | 1727 | 1702.3286 | 12.3357 |  | 140 | API Grade X52 | 350 | 31.0242 | 9432 | 350 | 9782 | 0.06645 | 0.52828 | 9508.9576 | 5.4255 | 1085.1061 | 10594.0637 | 212 | 10806.0637 | -1162.0637 | 12.32%
1700 | 1727 | 1700.4308 | 13.2846 |  | 130 | API Grade X52 | 350 | 33.448 | 10077 | 350 | 10427 | 0.071522 | 0.5686 | 10234.7488 | 5.4255 | 1085.1061 | 11319.8549 | 212 | 11531.8549 | -1242.8549 | 12.33%
1700 | 1727 | 1698.2167 | 14.3917 |  | 120 | API Grade X52 | 350 | 36.2826 | 10877 | 350 | 11227 | 0.077432 | 0.61558 | 11080.482 | 5.4255 | 1085.1061 | 12165.5881 | 212 | 12377.5881 | -1288.5881 | 11.85%
1800 | 1829 | 1806.1375 | 11.4313 |  | 160 | API Grade X52 | 350 | 27.0971 | 9313 | 700 | 10013 | 0.065273 | 0.51892 | 9340.585 | 5.746 | 1149.1946 | 10489.7796 | 212 | 10701.7796 | -1176.7796 | 12.64%
1800 | 1829 | 1804.6133 | 12.1933 |  | 150 | API Grade X52 | 350 | 28.928 | 9889 | 700 | 10589 | 0.069595 | 0.55328 | 9959.1132 | 5.746 | 1149.1946 | 11108.3078 | 212 | 11320.3078 | -1219.3078 | 12.33%
1800 | 1829 | 1802.8714 | 13.0643 |  | 140 | API Grade X52 | 350 | 31.0242 | 10507 | 700 | 11207 | 0.074531 | 0.59252 | 10665.3631 | 5.746 | 1149.1946 | 11814.5577 | 212 | 12026.5577 | -1307.5577 | 12.44%
1800 | 1829 | 1800.8615 | 14.0692 |  | 130 | API Grade X52 | 350 | 33.448 | 11285 | 700 | 11985 | 0.08022 | 0.63775 | 11479.4194 | 5.746 | 1149.1946 | 12628.614 | 212 | 12840.614 | -1343.614 | 11.91%
1800 | 1829 | 1798.5167 | 15.2417 |  | 120 | API Grade X52 | 350 | 36.2826 | 12055 | 700 | 12755 | 0.086848 | 0.69044 | 12428.0041 | 5.746 | 1149.1946 | 13577.1987 | 212 | 13789.1987 | -1522.1987 | 12.63%
1900 | 1930 | 1905.875 | 12.0625 |  | 160 | API Grade X52 | 350 | 27.0971 | 10388 | 700 | 11088 | 0.072681 | 0.57781 | 10400.6692 | 6.0633 | 1212.6548 | 11613.324 | 212 | 11825.324 | -1225.324 | 11.8%
1900 | 1930 | 1904.2667 | 12.8667 |  | 150 | API Grade X52 | 350 | 28.928 | 11058 | 700 | 11758 | 0.077494 | 0.61608 | 11089.3956 | 6.0633 | 1212.6548 | 12302.0503 | 212 | 12514.0503 | -1244.0503 | 11.25%
1900 | 1930 | 1902.4286 | 13.7857 |  | 140 | API Grade X52 | 350 | 31.0242 | 11779 | 700 | 12479 | 0.08299 | 0.65977 | 11875.7994 | 6.0633 | 1212.6548 | 13088.4542 | 212 | 13300.4542 | -1309.4542 | 11.12%
1900 | 1930 | 1900.3077 | 14.8462 |  | 130 | API Grade X52 | 350 | 33.448 | 12229 | 700 | 12929 | 0.089324 | 0.71012 | 12782.2448 | 6.0633 | 1212.6548 | 13994.8995 | 212 | 14206.8995 | -1765.8995 | 14.44%
2000 | 2032 | 2006.6 | 12.7 |  | 160 | API Grade X52 | 350 | 27.0971 | 11342 | 700 | 12042 | 0.080566 | 0.6405 | 11529.0646 | 6.3837 | 1276.7433 | 12805.8079 | 212 | 13017.8079 | -1463.8079 | 12.91%
2000 | 2032 | 2004.9067 | 13.5467 |  | 150 | API Grade X52 | 350 | 28.928 | 11994 | 700 | 12694 | 0.085902 | 0.68292 | 12292.5127 | 6.3837 | 1276.7433 | 13569.2559 | 212 | 13781.2559 | -1575.2559 | 13.13%
2000 | 2032 | 2002.9714 | 14.5143 |  | 140 | API Grade X52 | 350 | 31.0242 | 12778 | 700 | 13478 | 0.091993 | 0.73135 | 13164.2355 | 6.3837 | 1276.7433 | 14440.9787 | 212 | 14652.9787 | -1662.9787 | 13.01%
2100 | 2134 | 2107.325 | 13.3375 |  | 160 | API Grade X52 | 350 | 27.0971 | 12477 | 700 | 13177 | 0.088858 | 0.70642 | 12715.5601 | 6.7042 | 1340.8317 | 14056.3919 | 212 | 14268.3919 | -1579.3919 | 12.66%
2100 | 2134 | 2105.5467 | 14.2267 |  | 150 | API Grade X52 | 350 | 28.928 | 13361 | 700 | 14061 | 0.094742 | 0.7532 | 13557.5772 | 6.7042 | 1340.8317 | 14898.409 | 212 | 15110.409 | -1537.409 | 11.51%
2100 | 2134 | 2103.5143 | 15.2429 |  | 140 | API Grade X52 | 350 | 31.0242 | 14225 | 700 | 14925 | 0.10146 | 0.80661 | 14519.012 | 6.7042 | 1340.8317 | 15859.8438 | 212 | 16071.8438 | -1634.8438 | 11.49%
2200 | 2236 | 2208.05 | 13.975 |  | 160 | API Grade X52 | 350 | 27.0971 | 14030 | 700 | 14730 | 0.097555 | 0.77556 | 13960.1558 | 7.0246 | 1404.9202 | 15365.076 | 212 | 15577.076 | -1335.076 | 9.516%
2200 | 2236 | 2206.1867 | 14.9067 |  | 150 | API Grade X52 | 350 | 28.928 | 14852 | 700 | 15552 | 0.10402 | 0.82692 | 14884.5893 | 7.0246 | 1404.9202 | 16289.5095 | 212 | 16501.5095 | -1437.5095 | 9.679%
2300 | 2337 | 2307.7875 | 14.6062 |  | 160 | API Grade X52 | 350 | 27.0971 | 15130 | 700 | 15830 | 0.10657 | 0.84721 | 15249.798 | 7.3419 | 1468.3804 | 16718.1784 | 212 | 16930.1784 | -1588.1784 | 10.5%
2400 | 2450 | 2419.375 | 15.3125 |  | 160 | API Grade X52 | 350 | 27.0971 | 16490 | 700 | 17190 | 0.11712 | 0.93112 | 16760.186 | 7.6969 | 1539.3804 | 18299.5664 | 212 | 18511.5664 | -1809.5664 | 10.97%
500 | 508 | 498.7636 | 4.6182 |  | 110 | API Grade X65 | 350 | 39.6421 | 1364.2863 | 85 | 1449.2863 | 0.0073033 | 0.058061 | 1045.1005 | 1.5959 | 319.1858 | 1364.2863 | 85 | 1449.2863 | 0 | 0% |  | 18000
500 | 508 | 497.84 | 5.08 |  | 100 | API Grade X65 | 350 | 43.6872 | 1467.7417 | 85 | 1552.7417 | 0.0080262 | 0.063809 | 1148.5559 | 1.5959 | 319.1858 | 1467.7417 | 85 | 1552.7417 | 0 | 0%
600 | 610 | 601.2857 | 4.3571 |  | 140 | API Grade X65 | 448 | 39.711 | 1569.6108 | 85 | 1654.6108 | 0.0082903 | 0.065908 | 1186.3365 | 1.9164 | 383.2743 | 1569.6108 | 85 | 1654.6108 | 0 | 0%
600 | 610 | 600.6154 | 4.6923 |  | 130 | API Grade X65 | 448 | 42.8135 | 1660.1605 | 85 | 1745.1605 | 0.008923 | 0.070938 | 1276.8862 | 1.9164 | 383.2743 | 1660.1605 | 85 | 1745.1605 | 0 | 0%
600 | 610 | 599.8333 | 5.0833 |  | 120 | API Grade X65 | 448 | 46.4417 | 1765.6741 | 85 | 1850.6741 | 0.0096604 | 0.0768 | 1382.3997 | 1.9164 | 383.2743 | 1765.6741 | 85 | 1850.6741 | 0 | 0%
600 | 610 | 598.9091 | 5.5455 |  | 110 | API Grade X65 | 448 | 50.7419 | 1890.1947 | 85 | 1975.1947 | 0.010531 | 0.083718 | 1506.9204 | 1.9164 | 383.2743 | 1890.1947 | 85 | 1975.1947 | 0 | 0%
600 | 610 | 597.8 | 6.1 |  | 100 | API Grade X65 | 448 | 55.9196 | 2039.366 | 85 | 2124.366 | 0.011573 | 0.092005 | 1656.0917 | 1.9164 | 383.2743 | 2039.366 | 85 | 2124.366 | 0 | 0%
700 | 711 | 700.8429 | 5.0786 |  | 140 | API Grade X65 | 448 | 39.711 | 2099 | 85 | 2184 | 0.011263 | 0.08954 | 1611.712 | 2.2337 | 446.7345 | 2058.4465 | 213 | 2271.4465 | 40.5535 | -1.932%
700 | 711 | 700.0615 | 5.4692 |  | 130 | API Grade X65 | 448 | 42.8135 | 2201 | 85 | 2286 | 0.012122 | 0.096374 | 1734.7293 | 2.2337 | 446.7345 | 2181.4638 | 214 | 2395.4638 | 19.5362 | -0.8876%
700 | 711 | 699.15 | 5.925 |  | 120 | API Grade X65 | 448 | 46.4417 | 2303 | 85 | 2388 | 0.013124 | 0.10434 | 1878.0761 | 2.2337 | 446.7345 | 2324.8105 | 215 | 2539.8105 | -21.8105 | 0.947%
700 | 711 | 698.0727 | 6.4636 |  | 110 | API Grade X65 | 448 | 50.7419 | 2457 | 85 | 2542 | 0.014306 | 0.11374 | 2047.2451 | 2.2337 | 446.7345 | 2493.9796 | 216 | 2709.9796 | -36.9796 | 1.505%
700 | 711 | 696.78 | 7.11 |  | 100 | API Grade X65 | 448 | 55.9196 | 2619 | 85 | 2704 | 0.015723 | 0.12499 | 2249.9036 | 2.2337 | 446.7345 | 2696.638 | 217 | 2913.638 | -77.638 | 2.964%
800 | 813 | 802.8375 | 5.0812 |  | 160 | API Grade X65 | 448 | 34.6843 | 2387 | 110 | 2497 | 0.012897 | 0.10253 | 1845.5582 | 2.5541 | 510.823 | 2356.3812 | 218 | 2574.3812 | 30.6188 | -1.283%
800 | 813 | 802.16 | 5.42 |  | 150 | API Grade X65 | 448 | 37.0279 | 2475 | 110 | 2585 | 0.013751 | 0.10932 | 1967.7701 | 2.5541 | 510.823 | 2478.593 | 219 | 2697.593 | -3.593 | 0.1452%
800 | 813 | 801.3857 | 5.8071 |  | 140 | API Grade X65 | 448 | 39.711 | 2593 | 110 | 2703 | 0.014726 | 0.11707 | 2107.3144 | 2.5541 | 510.823 | 2618.1373 | 220 | 2838.1373 | -25.1373 | 0.9694%
800 | 813 | 800.4923 | 6.2538 |  | 130 | API Grade X65 | 448 | 42.8135 | 2740 | 110 | 2850 | 0.01585 | 0.12601 | 2268.1596 | 2.5541 | 510.823 | 2778.9825 | 221 | 2999.9825 | -38.9825 | 1.423%
800 | 813 | 799.45 | 6.775 |  | 120 | API Grade X65 | 448 | 46.4417 | 2886 | 110 | 2996 | 0.01716 | 0.13642 | 2455.5855 | 2.5541 | 510.823 | 2966.4085 | 222 | 3188.4085 | -80.4085 | 2.786%
800 | 813 | 798.2182 | 7.3909 |  | 110 | API Grade X65 | 448 | 50.7419 | 3062 | 110 | 3172 | 0.018706 | 0.14871 | 2676.7741 | 2.5541 | 510.823 | 3187.5971 | 223 | 3410.5971 | -125.5971 | 4.102%
800 | 813 | 796.74 | 8.13 |  | 100 | API Grade X65 | 448 | 55.9196 | 3269 | 110 | 3379 | 0.020557 | 0.16343 | 2941.7502 | 2.5541 | 510.823 | 3452.5732 | 224 | 3676.5732 | -183.5732 | 5.616%
900 | 914 | 902.575 | 5.7125 |  | 160 | API Grade X65 | 448 | 34.6843 | 2865 | 135 | 3000 | 0.0163 | 0.12959 | 2332.5935 | 2.8714 | 574.2831 | 2906.8766 | 225 | 3131.8766 | -41.8766 | 1.462%
900 | 914 | 901.8133 | 6.0933 |  | 150 | API Grade X65 | 448 | 37.0279 | 2997 | 135 | 3132 | 0.01738 | 0.13817 | 2487.0565 | 2.8714 | 574.2831 | 3061.3396 | 226 | 3287.3396 | -64.3396 | 2.147%
900 | 914 | 900.9429 | 6.5286 |  | 140 | API Grade X65 | 448 | 39.711 | 3129 | 135 | 3264 | 0.018612 | 0.14797 | 2663.426 | 2.8714 | 574.2831 | 3237.7091 | 227 | 3464.7091 | -108.7091 | 3.474%
900 | 914 | 899.9385 | 7.0308 |  | 130 | API Grade X65 | 448 | 42.8135 | 3294 | 135 | 3429 | 0.020033 | 0.15926 | 2866.7175 | 2.8714 | 574.2831 | 3441.0007 | 228 | 3669.0007 | -147.0007 | 4.463%
900 | 914 | 898.7667 | 7.6167 |  | 120 | API Grade X65 | 448 | 46.4417 | 3500 | 135 | 3635 | 0.021688 | 0.17242 | 3103.6045 | 2.8714 | 574.2831 | 3677.8876 | 229 | 3906.8876 | -177.8876 | 5.083%
900 | 914 | 897.3818 | 8.3091 |  | 110 | API Grade X65 | 448 | 50.7419 | 3734 | 135 | 3869 | 0.023642 | 0.18795 | 3383.1638 | 2.8714 | 574.2831 | 3957.4469 | 230 | 4187.4469 | -223.4469 | 5.984%
900 | 914 | 895.72 | 9.14 |  | 100 | API Grade X65 | 448 | 55.9196 | 3997 | 135 | 4132 | 0.025982 | 0.20656 | 3718.066 | 2.8714 | 574.2831 | 4292.3491 | 231 | 4523.3491 | -295.3491 | 7.389%
1000 | 1016 | 1003.3 | 6.35 |  | 160 | API Grade X65 | 448 | 34.6843 | 3470 | 170 | 3640 | 0.020142 | 0.16013 | 2882.2662 | 3.1919 | 638.3716 | 3520.6378 | 232 | 3752.6378 | -50.6378 | 1.459%
1000 | 1016 | 1002.4533 | 6.7733 |  | 150 | API Grade X65 | 448 | 37.0279 | 3617 | 170 | 3787 | 0.021475 | 0.17073 | 3073.1282 | 3.1919 | 638.3716 | 3711.4998 | 233 | 3944.4998 | -94.4998 | 2.613%
1000 | 1016 | 1001.4857 | 7.2571 |  | 140 | API Grade X65 | 448 | 39.711 | 3801 | 170 | 3971 | 0.022998 | 0.18284 | 3291.0589 | 3.1919 | 638.3716 | 3929.4305 | 234 | 4163.4305 | -128.4305 | 3.379%
1000 | 1016 | 1000.3692 | 7.8154 |  | 130 | API Grade X65 | 448 | 42.8135 | 3985 | 170 | 4155 | 0.024754 | 0.19679 | 3542.2559 | 3.1919 | 638.3716 | 4180.6275 | 235 | 4415.6275 | -195.6275 | 4.909%
1000 | 1016 | 999.0667 | 8.4667 |  | 120 | API Grade X65 | 448 | 46.4417 | 4246 | 170 | 4416 | 0.026799 | 0.21305 | 3834.9649 | 3.1919 | 638.3716 | 4473.3365 | 236 | 4709.3365 | -227.3365 | 5.354%
1000 | 1016 | 997.5273 | 9.2364 |  | 110 | API Grade X65 | 448 | 50.7419 | 4524 | 170 | 4694 | 0.029213 | 0.23224 | 4180.402 | 3.1919 | 638.3716 | 4818.7737 | 237 | 5055.7737 | -294.7737 | 6.516%
1000 | 1016 | 995.68 | 10.16 |  | 100 | API Grade X65 | 448 | 55.9196 | 4897 | 170 | 5067 | 0.032105 | 0.25523 | 4594.2235 | 3.1919 | 638.3716 | 5232.5951 | 238 | 5470.5951 | -335.5951 | 6.853%
1100 | 1118 | 1104.025 | 6.9875 |  | 160 | API Grade X65 | 448 | 34.6843 | 4053 | 225 | 4278 | 0.024389 | 0.19389 | 3490.0389 | 3.5123 | 702.4601 | 4192.4991 | 239 | 4431.4991 | -139.4991 | 3.442%
1100 | 1118 | 1103.0933 | 7.4533 |  | 150 | API Grade X65 | 448 | 37.0279 | 4255 | 225 | 4480 | 0.026004 | 0.20673 | 3721.1473 | 3.5123 | 702.4601 | 4423.6074 | 240 | 4663.6074 | -168.6074 | 3.963%
1100 | 1118 | 1102.0286 | 7.9857 |  | 140 | API Grade X65 | 448 | 39.711 | 4462 | 225 | 4687 | 0.027848 | 0.22139 | 3985.0323 | 3.5123 | 702.4601 | 4687.4924 | 241 | 4928.4924 | -225.4924 | 5.054%
1100 | 1118 | 1100.8 | 8.6 |  | 130 | API Grade X65 | 448 | 42.8135 | 4705 | 225 | 4930 | 0.029973 | 0.23829 | 4289.1982 | 3.5123 | 702.4601 | 4991.6584 | 242 | 5233.6584 | -286.6584 | 6.093%
1100 | 1118 | 1099.3667 | 9.3167 |  | 120 | API Grade X65 | 448 | 46.4417 | 5000 | 225 | 5225 | 0.03245 | 0.25798 | 4643.6297 | 3.5123 | 702.4601 | 5346.0898 | 243 | 5589.0898 | -346.0898 | 6.922%
1100 | 1118 | 1097.6727 | 10.1636 |  | 110 | API Grade X65 | 448 | 50.7419 | 5370 | 225 | 5595 | 0.035373 | 0.28122 | 5061.9079 | 3.5123 | 702.4601 | 5764.368 | 244 | 6008.368 | -394.368 | 7.344%
1100 | 1118 | 1095.64 | 11.18 |  | 100 | API Grade X65 | 448 | 55.9196 | 5775 | 225 | 6000 | 0.038875 | 0.30906 | 5562.9904 | 3.5123 | 702.4601 | 6265.4505 | 245 | 6510.4505 | -490.4505 | 8.493%
1200 | 1219 | 1203.7625 | 7.6188 |  | 160 | API Grade X65 | 448 | 34.6843 | 4667 | 225 | 4892 | 0.028994 | 0.23051 | 4149.1017 | 3.8296 | 765.9203 | 4915.022 | 246 | 5161.022 | -248.022 | 5.314%
1200 | 1219 | 1202.7467 | 8.1267 |  | 150 | API Grade X65 | 448 | 37.0279 | 4892 | 225 | 5117 | 0.030914 | 0.24577 | 4423.8528 | 3.8296 | 765.9203 | 5189.7731 | 247 | 5436.7731 | -297.7731 | 6.087%
1200 | 1219 | 1201.5857 | 8.7071 |  | 140 | API Grade X65 | 448 | 39.711 | 5157 | 225 | 5382 | 0.033107 | 0.2632 | 4737.5701 | 3.8296 | 765.9203 | 5503.4904 | 248 | 5751.4904 | -346.4904 | 6.719%
1200 | 1219 | 1200.2462 | 9.3769 |  | 130 | API Grade X65 | 448 | 42.8135 | 5506 | 225 | 5731 | 0.035634 | 0.28329 | 5099.1751 | 3.8296 | 765.9203 | 5865.0954 | 249 | 6114.0954 | -359.0954 | 6.522%
1200 | 1219 | 1198.6833 | 10.1583 |  | 120 | API Grade X65 | 448 | 46.4417 | 5867 | 225 | 6092 | 0.038578 | 0.3067 | 5520.5378 | 3.8296 | 765.9203 | 6286.4581 | 250 | 6536.4581 | -419.4581 | 7.149%
1200 | 1219 | 1196.8364 | 11.0818 |  | 110 | API Grade X65 | 448 | 50.7419 | 6376 | 225 | 6601 | 0.042053 | 0.33432 | 6017.8041 | 3.8296 | 765.9203 | 6783.7244 | 251 | 7034.7244 | -407.7244 | 6.395%
1200 | 1219 | 1194.62 | 12.19 |  | 100 | API Grade X65 | 448 | 55.9196 | 6879 | 225 | 7104 | 0.046216 | 0.36742 | 6613.5115 | 3.8296 | 765.9203 | 7379.4318 | 252 | 7631.4318 | -500.4318 | 7.275%
1300 | 1321 | 1304.4875 | 8.2562 |  | 160 | API Grade X65 | 448 | 34.6843 | 5395 | 225 | 5620 | 0.03405 | 0.27069 | 4872.5051 | 4.15 | 830.0088 | 5702.5139 | 253 | 5955.5139 | -307.5139 | 5.7%
1300 | 1321 | 1303.3867 | 8.8067 |  | 150 | API Grade X65 | 448 | 37.0279 | 5665 | 225 | 5890 | 0.036304 | 0.28862 | 5195.1596 | 4.15 | 830.0088 | 6025.1684 | 254 | 6279.1684 | -360.1684 | 6.358%
1300 | 1321 | 1302.1286 | 9.4357 |  | 140 | API Grade X65 | 448 | 39.711 | 5985 | 225 | 6210 | 0.038879 | 0.30909 | 5563.574 | 4.15 | 830.0088 | 6393.5828 | 255 | 6648.5828 | -408.5828 | 6.827%
1300 | 1321 | 1300.6769 | 10.1615 |  | 130 | API Grade X65 | 448 | 42.8135 | 6377 | 225 | 6602 | 0.041846 | 0.33268 | 5988.2255 | 4.15 | 830.0088 | 6818.2343 | 256 | 7074.2343 | -441.2343 | 6.919%
1300 | 1321 | 1298.9833 | 11.0083 |  | 120 | API Grade X65 | 448 | 46.4417 | 6760 | 225 | 6985 | 0.045304 | 0.36017 | 6483.0536 | 4.15 | 830.0088 | 7313.0624 | 257 | 7570.0624 | -553.0624 | 8.181%
1300 | 1321 | 1296.9818 | 12.0091 |  | 110 | API Grade X65 | 448 | 50.7419 | 7298 | 225 | 7523 | 0.049385 | 0.39261 | 7067.0192 | 4.15 | 830.0088 | 7897.0279 | 258 | 8155.0279 | -599.0279 | 8.208%
1300 | 1321 | 1294.58 | 13.21 |  | 100 | API Grade X65 | 448 | 55.9196 | 7800 | 225 | 8025 | 0.054274 | 0.43148 | 7766.5892 | 4.15 | 830.0088 | 8596.598 | 259 | 8855.598 | -796.598 | 10.21%
1400 | 1422 | 1404.225 | 8.8875 |  | 160 | API Grade X65 | 448 | 34.6843 | 6120 | 225 | 6345 | 0.039455 | 0.31367 | 5646.0648 | 4.4673 | 893.469 | 6539.5338 | 260 | 6799.5338 | -419.5338 | 6.855%
1400 | 1422 | 1403.04 | 9.48 |  | 150 | API Grade X65 | 448 | 37.0279 | 6446 | 225 | 6671 | 0.042068 | 0.33444 | 6019.944 | 4.4673 | 893.469 | 6913.4129 | 261 | 7174.4129 | -467.4129 | 7.251%
1400 | 1422 | 1401.6857 | 10.1571 |  | 140 | API Grade X65 | 448 | 39.711 | 6833 | 225 | 7058 | 0.045051 | 0.35816 | 6446.848 | 4.4673 | 893.469 | 7340.3169 | 262 | 7602.3169 | -507.3169 | 7.425%
1400 | 1422 | 1400.1231 | 10.9385 |  | 130 | API Grade X65 | 448 | 42.8135 | 7213 | 225 | 7438 | 0.04849 | 0.3855 | 6938.9172 | 4.4673 | 893.469 | 7832.3861 | 263 | 8095.3861 | -619.3861 | 8.587%
1400 | 1422 | 1398.3 | 11.85 |  | 120 | API Grade X65 | 448 | 46.4417 | 7773 | 225 | 7998 | 0.052497 | 0.41735 | 7512.3042 | 4.4673 | 893.469 | 8405.7732 | 264 | 8669.7732 | -632.7732 | 8.141%
1400 | 1422 | 1396.1455 | 12.9273 |  | 110 | API Grade X65 | 448 | 50.7419 | 8364 | 225 | 8589 | 0.057226 | 0.45494 | 8188.9803 | 4.4673 | 893.469 | 9082.4493 | 265 | 9347.4493 | -718.4493 | 8.59%
1400 | 1422 | 1393.56 | 14.22 |  | 100 | API Grade X65 | 448 | 55.9196 | 9125 | 225 | 9350 | 0.06289 | 0.49998 | 8999.6142 | 4.4673 | 893.469 | 9893.0832 | 266 | 10159.0832 | -768.0832 | 8.417%
1500 | 1524 | 1504.95 | 9.525 |  | 160 | API Grade X65 | 448 | 34.6843 | 6947 | 225 | 7172 | 0.045319 | 0.36028 | 6485.0988 | 4.7878 | 957.5574 | 7442.6563 | 267 | 7709.6563 | -495.6563 | 7.135%
1500 | 1524 | 1503.68 | 10.16 |  | 150 | API Grade X65 | 448 | 37.0279 | 7358 | 225 | 7583 | 0.04832 | 0.38414 | 6914.5384 | 4.7878 | 957.5574 | 7872.0958 | 268 | 8140.0958 | -514.0958 | 6.987%
1500 | 1524 | 1502.2286 | 10.8857 |  | 140 | API Grade X65 | 448 | 39.711 | 7830 | 225 | 8055 | 0.051746 | 0.41138 | 7404.8825 | 4.7878 | 957.5574 | 8362.4399 | 269 | 8631.4399 | -532.4399 | 6.8%
1500 | 1524 | 1500.5538 | 11.7231 |  | 130 | API Grade X65 | 448 | 42.8135 | 8285 | 225 | 8510 | 0.055696 | 0.44278 | 7970.0757 | 4.7878 | 957.5574 | 8927.6331 | 270 | 9197.6331 | -642.6331 | 7.757%
1500 | 1524 | 1498.6 | 12.7 |  | 120 | API Grade X65 | 448 | 46.4417 | 8884 | 225 | 9109 | 0.060298 | 0.47937 | 8628.671 | 4.7878 | 957.5574 | 9586.2284 | 271 | 9857.2284 | -702.2284 | 7.904%
1500 | 1524 | 1496.2909 | 13.8545 |  | 110 | API Grade X65 | 448 | 50.7419 | 9682 | 225 | 9907 | 0.06573 | 0.52255 | 9405.9046 | 4.7878 | 957.5574 | 10363.462 | 272 | 10635.462 | -681.462 | 7.038%
1500 | 1524 | 1493.52 | 15.24 |  | 100 | API Grade X65 | 448 | 55.9196 | 10636 | 225 | 10861 | 0.072236 | 0.57428 | 10337.0028 | 4.7878 | 957.5574 | 11294.5603 | 273 | 11567.5603 | -658.5603 | 6.192%
1600 | 1626 | 1605.675 | 10.1625 |  | 160 | API Grade X65 | 448 | 34.6843 | 7844 | 350 | 8194 | 0.051588 | 0.41012 | 7382.233 | 5.1082 | 1021.6459 | 8403.8789 | 274 | 8677.8789 | -559.8789 | 7.138%
1600 | 1626 | 1604.32 | 10.84 |  | 150 | API Grade X65 | 448 | 37.0279 | 8258 | 350 | 8608 | 0.055004 | 0.43728 | 7871.0802 | 5.1082 | 1021.6459 | 8892.7262 | 275 | 9167.7262 | -634.7262 | 7.686%
1600 | 1626 | 1602.7714 | 11.6143 |  | 140 | API Grade X65 | 448 | 39.711 | 8804 | 350 | 9154 | 0.058905 | 0.46829 | 8429.2574 | 5.1082 | 1021.6459 | 9450.9034 | 276 | 9726.9034 | -646.9034 | 7.348%
1600 | 1626 | 1600.9846 | 12.5077 |  | 130 | API Grade X65 | 448 | 42.8135 | 9361 | 350 | 9711 | 0.063401 | 0.50404 | 9072.6382 | 5.1082 | 1021.6459 | 10094.2842 | 277 | 10371.2842 | -733.2842 | 7.833%
1600 | 1626 | 1598.9 | 13.55 |  | 120 | API Grade X65 | 448 | 46.4417 | 10106 | 350 | 10456 | 0.06864 | 0.54569 | 9822.3422 | 5.1082 | 1021.6459 | 10843.9881 | 278 | 11121.9881 | -737.9881 | 7.302%
1600 | 1626 | 1596.4364 | 14.7818 |  | 110 | API Grade X65 | 448 | 50.7419 | 10904 | 350 | 11254 | 0.074822 | 0.59484 | 10707.0965 | 5.1082 | 1021.6459 | 11728.7424 | 279 | 12007.7424 | -824.7424 | 7.564%
1700 | 1727 | 1705.4125 | 10.7937 |  | 160 | API Grade X65 | 448 | 34.6843 | 8737 | 350 | 9087 | 0.058196 | 0.46266 | 8327.8202 | 5.4255 | 1085.1061 | 9412.9263 | 280 | 9692.9263 | -675.9263 | 7.736%
1700 | 1727 | 1703.9733 | 11.5133 |  | 150 | API Grade X65 | 448 | 37.0279 | 9211 | 350 | 9561 | 0.06205 | 0.49329 | 8879.2837 | 5.4255 | 1085.1061 | 9964.3898 | 281 | 10245.3898 | -753.3898 | 8.179%
1700 | 1727 | 1702.3286 | 12.3357 |  | 140 | API Grade X65 | 448 | 39.711 | 9779 | 350 | 10129 | 0.06645 | 0.52828 | 9508.9576 | 5.4255 | 1085.1061 | 10594.0637 | 282 | 10876.0637 | -815.0637 | 8.335%
1700 | 1727 | 1700.4308 | 13.2846 |  | 130 | API Grade X65 | 448 | 42.8135 | 10452 | 350 | 10802 | 0.071522 | 0.5686 | 10234.7488 | 5.4255 | 1085.1061 | 11319.8549 | 283 | 11602.8549 | -867.8549 | 8.303%
1700 | 1727 | 1698.2167 | 14.3917 |  | 120 | API Grade X65 | 448 | 46.4417 | 11282 | 350 | 11632 | 0.077432 | 0.61558 | 11080.482 | 5.4255 | 1085.1061 | 12165.5881 | 284 | 12449.5881 | -883.5881 | 7.832%
1800 | 1829 | 1806.1375 | 11.4313 |  | 160 | API Grade X65 | 448 | 34.6843 | 9655 | 700 | 10355 | 0.065273 | 0.51892 | 9340.585 | 5.746 | 1149.1946 | 10489.7796 | 285 | 10774.7796 | -834.7796 | 8.646%
1800 | 1829 | 1804.6133 | 12.1933 |  | 150 | API Grade X65 | 448 | 37.0279 | 10254 | 700 | 10954 | 0.069595 | 0.55328 | 9959.1132 | 5.746 | 1149.1946 | 11108.3078 | 286 | 11394.3078 | -854.3078 | 8.331%
1800 | 1829 | 1802.8714 | 13.0643 |  | 140 | API Grade X65 | 448 | 39.711 | 10898 | 700 | 11598 | 0.074531 | 0.59252 | 10665.3631 | 5.746 | 1149.1946 | 11814.5577 | 287 | 12101.5577 | -916.5577 | 8.41%
1800 | 1829 | 1800.8615 | 14.0692 |  | 130 | API Grade X65 | 448 | 42.8135 | 11705 | 700 | 12405 | 0.08022 | 0.63775 | 11479.4194 | 5.746 | 1149.1946 | 12628.614 | 288 | 12916.614 | -923.614 | 7.891%
1800 | 1829 | 1798.5167 | 15.2417 |  | 120 | API Grade X65 | 448 | 46.4417 | 12507 | 700 | 13207 | 0.086848 | 0.69044 | 12428.0041 | 5.746 | 1149.1946 | 13577.1987 | 289 | 13866.1987 | -1070.1987 | 8.557%
1900 | 1930 | 1905.875 | 12.0625 |  | 160 | API Grade X65 | 448 | 34.6843 | 10770 | 700 | 11470 | 0.072681 | 0.57781 | 10400.6692 | 6.0633 | 1212.6548 | 11613.324 | 290 | 11903.324 | -843.324 | 7.83%
1900 | 1930 | 1904.2667 | 12.8667 |  | 150 | API Grade X65 | 448 | 37.0279 | 11465 | 700 | 12165 | 0.077494 | 0.61608 | 11089.3956 | 6.0633 | 1212.6548 | 12302.0503 | 291 | 12593.0503 | -837.0503 | 7.301%
1900 | 1930 | 1902.4286 | 13.7857 |  | 140 | API Grade X65 | 448 | 39.711 | 12215 | 700 | 12915 | 0.08299 | 0.65977 | 11875.7994 | 6.0633 | 1212.6548 | 13088.4542 | 292 | 13380.4542 | -873.4542 | 7.151%
1900 | 1930 | 1900.3077 | 14.8462 |  | 130 | API Grade X65 | 448 | 42.8135 | 12695 | 700 | 13395 | 0.089324 | 0.71012 | 12782.2448 | 6.0633 | 1212.6548 | 13994.8995 | 293 | 14287.8995 | -1299.8995 | 10.24%
2000 | 2032 | 2006.6 | 12.7 |  | 160 | API Grade X65 | 448 | 34.6843 | 11764 | 700 | 12464 | 0.080566 | 0.6405 | 11529.0646 | 6.3837 | 1276.7433 | 12805.8079 | 294 | 13099.8079 | -1041.8079 | 8.856%
2000 | 2032 | 2004.9067 | 13.5467 |  | 150 | API Grade X65 | 448 | 37.0279 | 12441 | 700 | 13141 | 0.085902 | 0.68292 | 12292.5127 | 6.3837 | 1276.7433 | 13569.2559 | 295 | 13864.2559 | -1128.2559 | 9.069%
2000 | 2032 | 2002.9714 | 14.5143 |  | 140 | API Grade X65 | 448 | 39.711 | 13367 | 700 | 14067 | 0.091993 | 0.73135 | 13164.2355 | 6.3837 | 1276.7433 | 14440.9787 | 296 | 14736.9787 | -1073.9787 | 8.035%
2100 | 2134 | 2107.325 | 13.3375 |  | 160 | API Grade X65 | 448 | 34.6843 | 12940 | 700 | 13640 | 0.088858 | 0.70642 | 12715.5601 | 6.7042 | 1340.8317 | 14056.3919 | 297 | 14353.3919 | -1116.3919 | 8.627%
2100 | 2134 | 2105.5467 | 14.2267 |  | 150 | API Grade X65 | 448 | 37.0279 | 13856 | 700 | 14556 | 0.094742 | 0.7532 | 13557.5772 | 6.7042 | 1340.8317 | 14898.409 | 298 | 15196.409 | -1042.409 | 7.523%
2100 | 2134 | 2103.5143 | 15.2429 |  | 140 | API Grade X65 | 448 | 39.711 | 14754 | 700 | 15454 | 0.10146 | 0.80661 | 14519.012 | 6.7042 | 1340.8317 | 15859.8438 | 299 | 16158.8438 | -1105.8438 | 7.495%
2200 | 2236 | 2208.05 | 13.975 |  | 160 | API Grade X65 | 448 | 34.6843 | 14553 | 700 | 15253 | 0.097555 | 0.77556 | 13960.1558 | 7.0246 | 1404.9202 | 15365.076 | 300 | 15665.076 | -812.076 | 5.58%
2200 | 2236 | 2206.1867 | 14.9067 |  | 150 | API Grade X65 | 448 | 37.0279 | 15407 | 700 | 16107 | 0.10402 | 0.82692 | 14884.5893 | 7.0246 | 1404.9202 | 16289.5095 | 301 | 16590.5095 | -882.5095 | 5.728%
2300 | 2337 | 2307.7875 | 14.6062 |  | 160 | API Grade X65 | 448 | 34.6843 | 15688 | 700 | 16388 | 0.10657 | 0.84721 | 15249.798 | 7.3419 | 1468.3804 | 16718.1784 | 302 | 17020.1784 | -1030.1784 | 6.567%
2400 | 2450 | 2419.375 | 15.3125 |  | 160 | API Grade X65 | 448 | 34.6843 | 17205 | 700 | 17905 | 0.11712 | 0.93112 | 16760.186 | 7.6969 | 1539.3804 | 18299.5664 | 303 | 18602.5664 | -1094.5664 | 6.362%
Summary Table
Unique Code | ND | D/t | Grading | wt | ID | OD | Price (R/m) Delivered
500110API Grade X42 | 500 | 110 | API Grade X42 | 4.6182 | 498.7636 | 508 | 1420.2558 |  | 1
500100API Grade X42 | 500 | 100 | API Grade X42 | 5.08 | 497.84 | 508 | 1520.8374 |  | 1
600140API Grade X42 | 600 | 140 | API Grade X42 | 4.3571 | 601.2857 | 610 | 1621.657 |  | 1
600130API Grade X42 | 600 | 130 | API Grade X42 | 4.6923 | 600.6154 | 610 | 1709.6914 |  | 1
600120API Grade X42 | 600 | 120 | API Grade X42 | 5.0833 | 599.8333 | 610 | 1812.2741 |  | 1
600110API Grade X42 | 600 | 110 | API Grade X42 | 5.5455 | 598.9091 | 610 | 1933.3358 |  | 1
600100API Grade X42 | 600 | 100 | API Grade X42 | 6.1 | 597.8 | 610 | 2078.3634 |  | 1
700140API Grade X42 | 700 | 140 | API Grade X42 | 5.0786 | 700.8429 | 711 | 2098 |  | 1
700130API Grade X42 | 700 | 130 | API Grade X42 | 5.4692 | 700.0615 | 711 | 2194 |  | 1
700120API Grade X42 | 700 | 120 | API Grade X42 | 5.925 | 699.15 | 711 | 2290 |  | 1
700110API Grade X42 | 700 | 110 | API Grade X42 | 6.4636 | 698.0727 | 711 | 2434 |  | 1
700100API Grade X42 | 700 | 100 | API Grade X42 | 7.11 | 696.78 | 711 | 2586 |  | 1
800160API Grade X42 | 800 | 160 | API Grade X42 | 5.0812 | 802.8375 | 813 | 2400 |  | 1
800150API Grade X42 | 800 | 150 | API Grade X42 | 5.42 | 802.16 | 813 | 2483 |  | 1
800140API Grade X42 | 800 | 140 | API Grade X42 | 5.8071 | 801.3857 | 813 | 2592 |  | 1
800130API Grade X42 | 800 | 130 | API Grade X42 | 6.2538 | 800.4923 | 813 | 2730 |  | 1
800120API Grade X42 | 800 | 120 | API Grade X42 | 6.775 | 799.45 | 813 | 2867 |  | 1
800110API Grade X42 | 800 | 110 | API Grade X42 | 7.3909 | 798.2182 | 813 | 3031 |  | 1
800100API Grade X42 | 800 | 100 | API Grade X42 | 8.13 | 796.74 | 813 | 3226 |  | 1
900160API Grade X42 | 900 | 160 | API Grade X42 | 5.7125 | 902.575 | 914 | 2878 |  | 1
900150API Grade X42 | 900 | 150 | API Grade X42 | 6.0933 | 901.8133 | 914 | 3002 |  | 1
900140API Grade X42 | 900 | 140 | API Grade X42 | 6.5286 | 900.9429 | 914 | 3125 |  | 1
900130API Grade X42 | 900 | 130 | API Grade X42 | 7.0308 | 899.9385 | 914 | 3279 |  | 1
900120API Grade X42 | 900 | 120 | API Grade X42 | 7.6167 | 898.7667 | 914 | 3473 |  | 1
900110API Grade X42 | 900 | 110 | API Grade X42 | 8.3091 | 897.3818 | 914 | 3692 |  | 1
900100API Grade X42 | 900 | 100 | API Grade X42 | 9.14 | 895.72 | 914 | 3938 |  | 1
1000160API Grade X42 | 1000 | 160 | API Grade X42 | 6.35 | 1003.3 | 1016 | 3488 |  | 1
1000150API Grade X42 | 1000 | 150 | API Grade X42 | 6.7733 | 1002.4533 | 1016 | 3625 |  | 1
1000140API Grade X42 | 1000 | 140 | API Grade X42 | 7.2571 | 1001.4857 | 1016 | 3798 |  | 1
1000130API Grade X42 | 1000 | 130 | API Grade X42 | 7.8154 | 1000.3692 | 1016 | 3969 |  | 1
1000120API Grade X42 | 1000 | 120 | API Grade X42 | 8.4667 | 999.0667 | 1016 | 4214 |  | 1
1000110API Grade X42 | 1000 | 110 | API Grade X42 | 9.2364 | 997.5273 | 1016 | 4475 |  | 1
1000100API Grade X42 | 1000 | 100 | API Grade X42 | 10.16 | 995.68 | 1016 | 4825 |  | 1
1100160API Grade X42 | 1100 | 160 | API Grade X42 | 6.9875 | 1104.025 | 1118 | 4094 |  | 1
1100150API Grade X42 | 1100 | 150 | API Grade X42 | 7.4533 | 1103.0933 | 1118 | 4284 |  | 1
1100140API Grade X42 | 1100 | 140 | API Grade X42 | 7.9857 | 1102.0286 | 1118 | 4478 |  | 1
1100130API Grade X42 | 1100 | 130 | API Grade X42 | 8.6 | 1100.8 | 1118 | 4705 |  | 1
1100120API Grade X42 | 1100 | 120 | API Grade X42 | 9.3167 | 1099.3667 | 1118 | 4981 |  | 1
1100110API Grade X42 | 1100 | 110 | API Grade X42 | 10.1636 | 1097.6727 | 1118 | 5329 |  | 1
1100100API Grade X42 | 1100 | 100 | API Grade X42 | 11.18 | 1095.64 | 1118 | 5707 |  | 1
1200160API Grade X42 | 1200 | 160 | API Grade X42 | 7.6188 | 1203.7625 | 1219 | 4675 |  | 1
1200150API Grade X42 | 1200 | 150 | API Grade X42 | 8.1267 | 1202.7467 | 1219 | 4886 |  | 1
1200140API Grade X42 | 1200 | 140 | API Grade X42 | 8.7071 | 1201.5857 | 1219 | 5134 |  | 1
1200130API Grade X42 | 1200 | 130 | API Grade X42 | 9.3769 | 1200.2462 | 1219 | 5463 |  | 1
1200120API Grade X42 | 1200 | 120 | API Grade X42 | 10.1583 | 1198.6833 | 1219 | 5800 |  | 1
1200110API Grade X42 | 1200 | 110 | API Grade X42 | 11.0818 | 1196.8364 | 1219 | 6284 |  | 1
1200100API Grade X42 | 1200 | 100 | API Grade X42 | 12.19 | 1194.62 | 1219 | 6757 |  | 1
1300160API Grade X42 | 1300 | 160 | API Grade X42 | 8.2562 | 1304.4875 | 1321 | 5363 |  | 1
1300150API Grade X42 | 1300 | 150 | API Grade X42 | 8.8067 | 1303.3867 | 1321 | 5617 |  | 1
1300140API Grade X42 | 1300 | 140 | API Grade X42 | 9.4357 | 1302.1286 | 1321 | 5920 |  | 1
1300130API Grade X42 | 1300 | 130 | API Grade X42 | 10.1615 | 1300.6769 | 1321 | 6286 |  | 1
1300120API Grade X42 | 1300 | 120 | API Grade X42 | 11.0083 | 1298.9833 | 1321 | 6745 |  | 1
1300110API Grade X42 | 1300 | 110 | API Grade X42 | 12.0091 | 1296.9818 | 1321 | 7152 |  | 1
1300100API Grade X42 | 1300 | 100 | API Grade X42 | 13.21 | 1294.58 | 1321 | 7624 |  | 1
1400160API Grade X42 | 1400 | 160 | API Grade X42 | 8.8875 | 1404.225 | 1422 | 6048 |  | 1
1400150API Grade X42 | 1400 | 150 | API Grade X42 | 9.48 | 1403.04 | 1422 | 6354 |  | 1
1400140API Grade X42 | 1400 | 140 | API Grade X42 | 10.1571 | 1401.6857 | 1422 | 6719 |  | 1
1400130API Grade X42 | 1400 | 130 | API Grade X42 | 10.9385 | 1400.1231 | 1422 | 7076 |  | 1
1400120API Grade X42 | 1400 | 120 | API Grade X42 | 11.85 | 1398.3 | 1422 | 7602 |  | 1
1400110API Grade X42 | 1400 | 110 | API Grade X42 | 12.9273 | 1396.1455 | 1422 | 8160 |  | 1
1400100API Grade X42 | 1400 | 100 | API Grade X42 | 14.22 | 1393.56 | 1422 | 8880 |  | 1
1500160API Grade X42 | 1500 | 160 | API Grade X42 | 9.525 | 1504.95 | 1524 | 6832 |  | 1
1500150API Grade X42 | 1500 | 150 | API Grade X42 | 10.16 | 1503.68 | 1524 | 7209 |  | 1
1500140API Grade X42 | 1500 | 140 | API Grade X42 | 10.8857 | 1502.2286 | 1524 | 7665 |  | 1
1500130API Grade X42 | 1500 | 130 | API Grade X42 | 11.7231 | 1500.5538 | 1524 | 8105 |  | 1
1500120API Grade X42 | 1500 | 120 | API Grade X42 | 12.7 | 1498.6 | 1524 | 8631 |  | 1
1500110API Grade X42 | 1500 | 110 | API Grade X42 | 13.8545 | 1496.2909 | 1524 | 9411 |  | 1
1500100API Grade X42 | 1500 | 100 | API Grade X42 | 15.24 | 1493.52 | 1524 | 10320 |  | 1
1600160API Grade X42 | 1600 | 160 | API Grade X42 | 10.1625 | 1605.675 | 1626 | 7805 |  | 1
1600150API Grade X42 | 1600 | 150 | API Grade X42 | 10.84 | 1604.32 | 1626 | 8196 |  | 1
1600140API Grade X42 | 1600 | 140 | API Grade X42 | 11.6143 | 1602.7714 | 1626 | 8713 |  | 1
1600130API Grade X42 | 1600 | 130 | API Grade X42 | 12.5077 | 1600.9846 | 1626 | 9235 |  | 1
1600120API Grade X42 | 1600 | 120 | API Grade X42 | 13.55 | 1598.9 | 1626 | 9938 |  | 1
1600110API Grade X42 | 1600 | 110 | API Grade X42 | 14.7818 | 1596.4364 | 1626 | 10691 |  | 1
1600100API Grade X42 | 1600 | 100 | API Grade X42 | 16.26 | 1593.48 | 1626 | 11670 |  | 1
1700160API Grade X42 | 1700 | 160 | API Grade X42 | 10.7937 | 1705.4125 | 1727 | 8650 |  | 1
1700150API Grade X42 | 1700 | 150 | API Grade X42 | 11.5133 | 1703.9733 | 1727 | 9096 |  | 1
1700140API Grade X42 | 1700 | 140 | API Grade X42 | 12.3357 | 1702.3286 | 1727 | 9631 |  | 1
1700130API Grade X42 | 1700 | 130 | API Grade X42 | 13.2846 | 1700.4308 | 1727 | 10264 |  | 1
1700120API Grade X42 | 1700 | 120 | API Grade X42 | 14.3917 | 1698.2167 | 1727 | 11051 |  | 1
1700110API Grade X42 | 1700 | 110 | API Grade X42 | 15.7 | 1695.6 | 1727 | 11965 |  | 1
1700100API Grade X42 | 1700 | 100 | API Grade X42 | 17.27 | 1692.46 | 1727 | 13121 |  | 1
1800160API Grade X42 | 1800 | 160 | API Grade X42 | 11.4313 | 1806.1375 | 1829 | 9866 |  | 1
1800150API Grade X42 | 1800 | 150 | API Grade X42 | 12.1933 | 1804.6133 | 1829 | 10431 |  | 1
1800140API Grade X42 | 1800 | 140 | API Grade X42 | 13.0643 | 1802.8714 | 1829 | 11037 |  | 1
1800130API Grade X42 | 1800 | 130 | API Grade X42 | 14.0692 | 1800.8615 | 1829 | 11801 |  | 1
1800120API Grade X42 | 1800 | 120 | API Grade X42 | 15.2417 | 1798.5167 | 1829 | 12557 |  | 1
1800110API Grade X42 | 1800 | 110 | API Grade X42 | 16.6273 | 1795.7455 | 1829 | 13607 |  | 1
1800100API Grade X42 | 1800 | 100 | API Grade X42 | 18.29 | 1792.42 | 1829 | 14932 |  | 1
1900160API Grade X42 | 1900 | 160 | API Grade X42 | 12.0625 | 1905.875 | 1930 | 10922 |  | 1
1900150API Grade X42 | 1900 | 150 | API Grade X42 | 12.8667 | 1904.2667 | 1930 | 11581 |  | 1
1900140API Grade X42 | 1900 | 140 | API Grade X42 | 13.7857 | 1902.4286 | 1930 | 12290 |  | 1
1900130API Grade X42 | 1900 | 130 | API Grade X42 | 14.8462 | 1900.3077 | 1930 | 12727 |  | 1
1900120API Grade X42 | 1900 | 120 | API Grade X42 | 16.0833 | 1897.8333 | 1930 | 13938 |  | 1
1900110API Grade X42 | 1900 | 110 | API Grade X42 | 17.5455 | 1894.9091 | 1930 | 14977 |  | 1
1900100API Grade X42 | 1900 | 100 | API Grade X42 | 19.3 | 1891.4 | 1930 | 16308 |  | 1
2000160API Grade X42 | 2000 | 160 | API Grade X42 | 12.7 | 2006.6 | 2032 | 11859 |  | 1
2000150API Grade X42 | 2000 | 150 | API Grade X42 | 13.5467 | 2004.9067 | 2032 | 12498 |  | 1
2000140API Grade X42 | 2000 | 140 | API Grade X42 | 14.5143 | 2002.9714 | 2032 | 13377 |  | 1
2000130API Grade X42 | 2000 | 130 | API Grade X42 | 15.6308 | 2000.7385 | 2032 | 14238 |  | 1
2000120API Grade X42 | 2000 | 120 | API Grade X42 | 16.9333 | 1998.1333 | 2032 | 15141 |  | 1
2000110API Grade X42 | 2000 | 110 | API Grade X42 | 18.4727 | 1995.0545 | 2032 | 16516 |  | 1
2000100API Grade X42 | 2000 | 100 | API Grade X42 | 20.32 | 1991.36 | 2032 | 17951 |  | 1
2100160API Grade X42 | 2100 | 160 | API Grade X42 | 13.3375 | 2107.325 | 2134 | 12975 |  | 1
2100150API Grade X42 | 2100 | 150 | API Grade X42 | 14.2267 | 2105.5467 | 2134 | 13845 |  | 1
2100140API Grade X42 | 2100 | 140 | API Grade X42 | 15.2429 | 2103.5143 | 2134 | 14695 |  | 1
2100130API Grade X42 | 2100 | 130 | API Grade X42 | 16.4154 | 2101.1692 | 2134 | 15509 |  | 1
2100120API Grade X42 | 2100 | 120 | API Grade X42 | 17.7833 | 2098.4333 | 2134 | 16739 |  | 1
2100110API Grade X42 | 2100 | 110 | API Grade X42 | 19.4 | 2095.2 | 2134 | 17993 |  | 1
2100100API Grade X42 | 2100 | 100 | API Grade X42 | 21.34 | 2091.32 | 2134 | 19475 |  | 1
2200160API Grade X42 | 2200 | 160 | API Grade X42 | 13.975 | 2208.05 | 2236 | 14503 |  | 1
2200150API Grade X42 | 2200 | 150 | API Grade X42 | 14.9067 | 2206.1867 | 2236 | 15311 |  | 1
2200140API Grade X42 | 2200 | 140 | API Grade X42 | 15.9714 | 2204.0571 | 2236 | 16300 |  | 1
2200130API Grade X42 | 2200 | 130 | API Grade X42 | 17.2 | 2201.6 | 2236 | 17484 |  | 1
2200120API Grade X42 | 2200 | 120 | API Grade X42 | 18.6333 | 2198.7333 | 2236 | 18441 |  | 1
2200110API Grade X42 | 2200 | 110 | API Grade X42 | 20.3273 | 2195.3455 | 2236 | 20179 |  | 1
2300160API Grade X42 | 2300 | 160 | API Grade X42 | 14.6062 | 2307.7875 | 2337 | 15580 |  | 1
2300150API Grade X42 | 2300 | 150 | API Grade X42 | 15.58 | 2305.84 | 2337 | 16477 |  | 1
2300140API Grade X42 | 2300 | 140 | API Grade X42 | 16.6929 | 2303.6143 | 2337 | 17459 |  | 1
2300130API Grade X42 | 2300 | 130 | API Grade X42 | 17.9769 | 2301.0462 | 2337 | 18615 |  | 1
2300120API Grade X42 | 2300 | 120 | API Grade X42 | 19.475 | 2298.05 | 2337 | 19949 |  | 1
2300110API Grade X42 | 2300 | 110 | API Grade X42 | 21.2455 | 2294.5091 | 2337 | 21465 |  | 1
2400160API Grade X42 | 2400 | 160 | API Grade X42 | 15.3125 | 2419.375 | 2450 | 16924 |  | 1
2400150API Grade X42 | 2400 | 150 | API Grade X42 | 16.3333 | 2417.3333 | 2450 | 17865 |  | 1
2400140API Grade X42 | 2400 | 140 | API Grade X42 | 17.5 | 2415 | 2450 | 18988 |  | 1
2400130API Grade X42 | 2400 | 130 | API Grade X42 | 18.8462 | 2412.3077 | 2450 | 20567 |  | 1
2400120API Grade X42 | 2400 | 120 | API Grade X42 | 20.4167 | 2409.1667 | 2450 | 21714 |  | 1
2500160API Grade X42 | 2500 | 160 | API Grade X42 | 15.875 | 2508.25 | 2540 | 18095 |  | 1
2500150API Grade X42 | 2500 | 150 | API Grade X42 | 16.9333 | 2506.1333 | 2540 | 19082 |  | 1
2500140API Grade X42 | 2500 | 140 | API Grade X42 | 18.1429 | 2503.7143 | 2540 | 20262 |  | 1
2500130API Grade X42 | 2500 | 130 | API Grade X42 | 19.5385 | 2500.9231 | 2540 | 21639 |  | 1
2500120API Grade X42 | 2500 | 120 | API Grade X42 | 21.1667 | 2497.6667 | 2540 | 23308 |  | 1
500110API Grade X52 | 500 | 110 | API Grade X52 | 4.6182 | 498.7636 | 508 | 1449.2863 |  | 1
500100API Grade X52 | 500 | 100 | API Grade X52 | 5.08 | 497.84 | 508 | 1552.7417 |  | 1
600140API Grade X52 | 600 | 140 | API Grade X52 | 4.3571 | 601.2857 | 610 | 1654.6108 |  | 1
600130API Grade X52 | 600 | 130 | API Grade X52 | 4.6923 | 600.6154 | 610 | 1745.1605 |  | 1
600120API Grade X52 | 600 | 120 | API Grade X52 | 5.0833 | 599.8333 | 610 | 1850.6741 |  | 1
600110API Grade X52 | 600 | 110 | API Grade X52 | 5.5455 | 598.9091 | 610 | 1975.1947 |  | 1
600100API Grade X52 | 600 | 100 | API Grade X52 | 6.1 | 597.8 | 610 | 2124.366 |  | 1
700140API Grade X52 | 700 | 140 | API Grade X52 | 5.0786 | 700.8429 | 711 | 2154 |  | 1
700130API Grade X52 | 700 | 130 | API Grade X52 | 5.4692 | 700.0615 | 711 | 2222 |  | 1
700120API Grade X52 | 700 | 120 | API Grade X52 | 5.925 | 699.15 | 711 | 2320 |  | 1
700110API Grade X52 | 700 | 110 | API Grade X52 | 6.4636 | 698.0727 | 711 | 2466 |  | 1
700100API Grade X52 | 700 | 100 | API Grade X52 | 7.11 | 696.78 | 711 | 2622 |  | 1
800160API Grade X52 | 800 | 160 | API Grade X52 | 5.0812 | 802.8375 | 813 | 2430 |  | 1
800150API Grade X52 | 800 | 150 | API Grade X52 | 5.42 | 802.16 | 813 | 2514 |  | 1
800140API Grade X52 | 800 | 140 | API Grade X52 | 5.8071 | 801.3857 | 813 | 2626 |  | 1
800130API Grade X52 | 800 | 130 | API Grade X52 | 6.2538 | 800.4923 | 813 | 2766 |  | 1
800120API Grade X52 | 800 | 120 | API Grade X52 | 6.775 | 799.45 | 813 | 2906 |  | 1
800110API Grade X52 | 800 | 110 | API Grade X52 | 7.3909 | 798.2182 | 813 | 3074 |  | 1
800100API Grade X52 | 800 | 100 | API Grade X52 | 8.13 | 796.74 | 813 | 3272 |  | 1
900160API Grade X52 | 900 | 160 | API Grade X52 | 5.7125 | 902.575 | 914 | 2914 |  | 1
900150API Grade X52 | 900 | 150 | API Grade X52 | 6.0933 | 901.8133 | 914 | 3041 |  | 1
900140API Grade X52 | 900 | 140 | API Grade X52 | 6.5286 | 900.9429 | 914 | 3167 |  | 1
900130API Grade X52 | 900 | 130 | API Grade X52 | 7.0308 | 899.9385 | 914 | 3325 |  | 1
900120API Grade X52 | 900 | 120 | API Grade X52 | 7.6167 | 898.7667 | 914 | 3522 |  | 1
900110API Grade X52 | 900 | 110 | API Grade X52 | 8.3091 | 897.3818 | 914 | 3745 |  | 1
900100API Grade X52 | 900 | 100 | API Grade X52 | 9.14 | 895.72 | 914 | 3996 |  | 1
1000160API Grade X52 | 1000 | 160 | API Grade X52 | 6.35 | 1003.3 | 1016 | 3533 |  | 1
1000150API Grade X52 | 1000 | 150 | API Grade X52 | 6.7733 | 1002.4533 | 1016 | 3675 |  | 1
1000140API Grade X52 | 1000 | 140 | API Grade X52 | 7.2571 | 1001.4857 | 1016 | 3850 |  | 1
1000130API Grade X52 | 1000 | 130 | API Grade X52 | 7.8154 | 1000.3692 | 1016 | 4026 |  | 1
1000120API Grade X52 | 1000 | 120 | API Grade X52 | 8.4667 | 999.0667 | 1016 | 4275 |  | 1
1000110API Grade X52 | 1000 | 110 | API Grade X52 | 9.2364 | 997.5273 | 1016 | 4541 |  | 1
1000100API Grade X52 | 1000 | 100 | API Grade X52 | 10.16 | 995.68 | 1016 | 4898 |  | 1
1100160API Grade X52 | 1100 | 160 | API Grade X52 | 6.9875 | 1104.025 | 1118 | 4150 |  | 1
1100150API Grade X52 | 1100 | 150 | API Grade X52 | 7.4533 | 1103.0933 | 1118 | 4343 |  | 1
1100140API Grade X52 | 1100 | 140 | API Grade X52 | 7.9857 | 1102.0286 | 1118 | 4541 |  | 1
1100130API Grade X52 | 1100 | 130 | API Grade X52 | 8.6 | 1100.8 | 1118 | 4773 |  | 1
1100120API Grade X52 | 1100 | 120 | API Grade X52 | 9.3167 | 1099.3667 | 1118 | 5055 |  | 1
1100110API Grade X52 | 1100 | 110 | API Grade X52 | 10.1636 | 1097.6727 | 1118 | 5410 |  | 1
1100100API Grade X52 | 1100 | 100 | API Grade X52 | 11.18 | 1095.64 | 1118 | 5795 |  | 1
1200160API Grade X52 | 1200 | 160 | API Grade X52 | 7.6188 | 1203.7625 | 1219 | 4740 |  | 1
1200150API Grade X52 | 1200 | 150 | API Grade X52 | 8.1267 | 1202.7467 | 1219 | 4955 |  | 1
1200140API Grade X52 | 1200 | 140 | API Grade X52 | 8.7071 | 1201.5857 | 1219 | 5209 |  | 1
1200130API Grade X52 | 1200 | 130 | API Grade X52 | 9.3769 | 1200.2462 | 1219 | 5543 |  | 1
1200120API Grade X52 | 1200 | 120 | API Grade X52 | 10.1583 | 1198.6833 | 1219 | 5888 |  | 1
1200110API Grade X52 | 1200 | 110 | API Grade X52 | 11.0818 | 1196.8364 | 1219 | 6380 |  | 1
1200100API Grade X52 | 1200 | 100 | API Grade X52 | 12.19 | 1194.62 | 1219 | 6862 |  | 1
1300160API Grade X52 | 1300 | 160 | API Grade X52 | 8.2562 | 1304.4875 | 1321 | 5440 |  | 1
1300150API Grade X52 | 1300 | 150 | API Grade X52 | 8.8067 | 1303.3867 | 1321 | 5699 |  | 1
1300140API Grade X52 | 1300 | 140 | API Grade X52 | 9.4357 | 1302.1286 | 1321 | 6007 |  | 1
1300130API Grade X52 | 1300 | 130 | API Grade X52 | 10.1615 | 1300.6769 | 1321 | 6381 |  | 1
1300120API Grade X52 | 1300 | 120 | API Grade X52 | 11.0083 | 1298.9833 | 1321 | 6747 |  | 1
1300110API Grade X52 | 1300 | 110 | API Grade X52 | 12.0091 | 1296.9818 | 1321 | 7265 |  | 1
1300100API Grade X52 | 1300 | 100 | API Grade X52 | 13.21 | 1294.58 | 1321 | 7745 |  | 1
1400160API Grade X52 | 1400 | 160 | API Grade X52 | 8.8875 | 1404.225 | 1422 | 6140 |  | 1
1400150API Grade X52 | 1400 | 150 | API Grade X52 | 9.48 | 1403.04 | 1422 | 6450 |  | 1
1400140API Grade X52 | 1400 | 140 | API Grade X52 | 10.1571 | 1401.6857 | 1422 | 6821 |  | 1
1400130API Grade X52 | 1400 | 130 | API Grade X52 | 10.9385 | 1400.1231 | 1422 | 7185 |  | 1
1400120API Grade X52 | 1400 | 120 | API Grade X52 | 11.85 | 1398.3 | 1422 | 7722 |  | 1
1400110API Grade X52 | 1400 | 110 | API Grade X52 | 12.9273 | 1396.1455 | 1422 | 8290 |  | 1
1400100API Grade X52 | 1400 | 100 | API Grade X52 | 14.22 | 1393.56 | 1422 | 9022 |  | 1
1500160API Grade X52 | 1500 | 160 | API Grade X52 | 9.525 | 1504.95 | 1524 | 6935 |  | 1
1500150API Grade X52 | 1500 | 150 | API Grade X52 | 10.16 | 1503.68 | 1524 | 7328 |  | 1
1500140API Grade X52 | 1500 | 140 | API Grade X52 | 10.8857 | 1502.2286 | 1524 | 7782 |  | 1
1500130API Grade X52 | 1500 | 130 | API Grade X52 | 11.7231 | 1500.5538 | 1524 | 8219 |  | 1
1500120API Grade X52 | 1500 | 120 | API Grade X52 | 12.7 | 1498.6 | 1524 | 8793 |  | 1
1500110API Grade X52 | 1500 | 110 | API Grade X52 | 13.8545 | 1496.2909 | 1524 | 9561 |  | 1
1500100API Grade X52 | 1500 | 100 | API Grade X52 | 15.24 | 1493.52 | 1524 | 10483 |  | 1
1600160API Grade X52 | 1600 | 160 | API Grade X52 | 10.1625 | 1605.675 | 1626 | 7923 |  | 1
1600150API Grade X52 | 1600 | 150 | API Grade X52 | 10.84 | 1604.32 | 1626 | 8320 |  | 1
1600140API Grade X52 | 1600 | 140 | API Grade X52 | 11.6143 | 1602.7714 | 1626 | 8845 |  | 1
1600130API Grade X52 | 1600 | 130 | API Grade X52 | 12.5077 | 1600.9846 | 1626 | 9379 |  | 1
1600120API Grade X52 | 1600 | 120 | API Grade X52 | 13.55 | 1598.9 | 1626 | 10095 |  | 1
1600110API Grade X52 | 1600 | 110 | API Grade X52 | 14.7818 | 1596.4364 | 1626 | 10861 |  | 1
1700160API Grade X52 | 1700 | 160 | API Grade X52 | 10.7937 | 1705.4125 | 1727 | 8782 |  | 1
1700150API Grade X52 | 1700 | 150 | API Grade X52 | 11.5133 | 1703.9733 | 1727 | 9236 |  | 1
1700140API Grade X52 | 1700 | 140 | API Grade X52 | 12.3357 | 1702.3286 | 1727 | 9782 |  | 1
1700130API Grade X52 | 1700 | 130 | API Grade X52 | 13.2846 | 1700.4308 | 1727 | 10427 |  | 1
1700120API Grade X52 | 1700 | 120 | API Grade X52 | 14.3917 | 1698.2167 | 1727 | 11227 |  | 1
1800160API Grade X52 | 1800 | 160 | API Grade X52 | 11.4313 | 1806.1375 | 1829 | 10013 |  | 1
1800150API Grade X52 | 1800 | 150 | API Grade X52 | 12.1933 | 1804.6133 | 1829 | 10589 |  | 1
1800140API Grade X52 | 1800 | 140 | API Grade X52 | 13.0643 | 1802.8714 | 1829 | 11207 |  | 1
1800130API Grade X52 | 1800 | 130 | API Grade X52 | 14.0692 | 1800.8615 | 1829 | 11985 |  | 1
1800120API Grade X52 | 1800 | 120 | API Grade X52 | 15.2417 | 1798.5167 | 1829 | 12755 |  | 1
1900160API Grade X52 | 1900 | 160 | API Grade X52 | 12.0625 | 1905.875 | 1930 | 11088 |  | 1
1900150API Grade X52 | 1900 | 150 | API Grade X52 | 12.8667 | 1904.2667 | 1930 | 11758 |  | 1
1900140API Grade X52 | 1900 | 140 | API Grade X52 | 13.7857 | 1902.4286 | 1930 | 12479 |  | 1
1900130API Grade X52 | 1900 | 130 | API Grade X52 | 14.8462 | 1900.3077 | 1930 | 12929 |  | 1
2000160API Grade X52 | 2000 | 160 | API Grade X52 | 12.7 | 2006.6 | 2032 | 12042 |  | 1
2000150API Grade X52 | 2000 | 150 | API Grade X52 | 13.5467 | 2004.9067 | 2032 | 12694 |  | 1
2000140API Grade X52 | 2000 | 140 | API Grade X52 | 14.5143 | 2002.9714 | 2032 | 13478 |  | 1
2100160API Grade X52 | 2100 | 160 | API Grade X52 | 13.3375 | 2107.325 | 2134 | 13177 |  | 1
2100150API Grade X52 | 2100 | 150 | API Grade X52 | 14.2267 | 2105.5467 | 2134 | 14061 |  | 1
2100140API Grade X52 | 2100 | 140 | API Grade X52 | 15.2429 | 2103.5143 | 2134 | 14925 |  | 1
2200160API Grade X52 | 2200 | 160 | API Grade X52 | 13.975 | 2208.05 | 2236 | 14730 |  | 1
2200150API Grade X52 | 2200 | 150 | API Grade X52 | 14.9067 | 2206.1867 | 2236 | 15552 |  | 1
2300160API Grade X52 | 2300 | 160 | API Grade X52 | 14.6062 | 2307.7875 | 2337 | 15830 |  | 1
2400160API Grade X52 | 2400 | 160 | API Grade X52 | 15.3125 | 2419.375 | 2450 | 17190 |  | 1
500110API Grade X65 | 500 | 110 | API Grade X65 | 4.6182 | 498.7636 | 508 | 1449.2863 |  | 1
500100API Grade X65 | 500 | 100 | API Grade X65 | 5.08 | 497.84 | 508 | 1552.7417 |  | 1
600140API Grade X65 | 600 | 140 | API Grade X65 | 4.3571 | 601.2857 | 610 | 1654.6108 |  | 1
600130API Grade X65 | 600 | 130 | API Grade X65 | 4.6923 | 600.6154 | 610 | 1745.1605 |  | 1
600120API Grade X65 | 600 | 120 | API Grade X65 | 5.0833 | 599.8333 | 610 | 1850.6741 |  | 1
600110API Grade X65 | 600 | 110 | API Grade X65 | 5.5455 | 598.9091 | 610 | 1975.1947 |  | 1
600100API Grade X65 | 600 | 100 | API Grade X65 | 6.1 | 597.8 | 610 | 2124.366 |  | 1
700140API Grade X65 | 700 | 140 | API Grade X65 | 5.0786 | 700.8429 | 711 | 2184 |  | 1
700130API Grade X65 | 700 | 130 | API Grade X65 | 5.4692 | 700.0615 | 711 | 2286 |  | 1
700120API Grade X65 | 700 | 120 | API Grade X65 | 5.925 | 699.15 | 711 | 2388 |  | 1
700110API Grade X65 | 700 | 110 | API Grade X65 | 6.4636 | 698.0727 | 711 | 2542 |  | 1
700100API Grade X65 | 700 | 100 | API Grade X65 | 7.11 | 696.78 | 711 | 2704 |  | 1
800160API Grade X65 | 800 | 160 | API Grade X65 | 5.0812 | 802.8375 | 813 | 2497 |  | 1
800150API Grade X65 | 800 | 150 | API Grade X65 | 5.42 | 802.16 | 813 | 2585 |  | 1
800140API Grade X65 | 800 | 140 | API Grade X65 | 5.8071 | 801.3857 | 813 | 2703 |  | 1
800130API Grade X65 | 800 | 130 | API Grade X65 | 6.2538 | 800.4923 | 813 | 2850 |  | 1
800120API Grade X65 | 800 | 120 | API Grade X65 | 6.775 | 799.45 | 813 | 2996 |  | 1
800110API Grade X65 | 800 | 110 | API Grade X65 | 7.3909 | 798.2182 | 813 | 3172 |  | 1
800100API Grade X65 | 800 | 100 | API Grade X65 | 8.13 | 796.74 | 813 | 3379 |  | 1
900160API Grade X65 | 900 | 160 | API Grade X65 | 5.7125 | 902.575 | 914 | 3000 |  | 1
900150API Grade X65 | 900 | 150 | API Grade X65 | 6.0933 | 901.8133 | 914 | 3132 |  | 1
900140API Grade X65 | 900 | 140 | API Grade X65 | 6.5286 | 900.9429 | 914 | 3264 |  | 1
900130API Grade X65 | 900 | 130 | API Grade X65 | 7.0308 | 899.9385 | 914 | 3429 |  | 1
900120API Grade X65 | 900 | 120 | API Grade X65 | 7.6167 | 898.7667 | 914 | 3635 |  | 1
900110API Grade X65 | 900 | 110 | API Grade X65 | 8.3091 | 897.3818 | 914 | 3869 |  | 1
900100API Grade X65 | 900 | 100 | API Grade X65 | 9.14 | 895.72 | 914 | 4132 |  | 1
1000160API Grade X65 | 1000 | 160 | API Grade X65 | 6.35 | 1003.3 | 1016 | 3640 |  | 1
1000150API Grade X65 | 1000 | 150 | API Grade X65 | 6.7733 | 1002.4533 | 1016 | 3787 |  | 1
1000140API Grade X65 | 1000 | 140 | API Grade X65 | 7.2571 | 1001.4857 | 1016 | 3971 |  | 1
1000130API Grade X65 | 1000 | 130 | API Grade X65 | 7.8154 | 1000.3692 | 1016 | 4155 |  | 1
1000120API Grade X65 | 1000 | 120 | API Grade X65 | 8.4667 | 999.0667 | 1016 | 4416 |  | 1
1000110API Grade X65 | 1000 | 110 | API Grade X65 | 9.2364 | 997.5273 | 1016 | 4694 |  | 1
1000100API Grade X65 | 1000 | 100 | API Grade X65 | 10.16 | 995.68 | 1016 | 5067 |  | 1
1100160API Grade X65 | 1100 | 160 | API Grade X65 | 6.9875 | 1104.025 | 1118 | 4278 |  | 1
1100150API Grade X65 | 1100 | 150 | API Grade X65 | 7.4533 | 1103.0933 | 1118 | 4480 |  | 1
1100140API Grade X65 | 1100 | 140 | API Grade X65 | 7.9857 | 1102.0286 | 1118 | 4687 |  | 1
1100130API Grade X65 | 1100 | 130 | API Grade X65 | 8.6 | 1100.8 | 1118 | 4930 |  | 1
1100120API Grade X65 | 1100 | 120 | API Grade X65 | 9.3167 | 1099.3667 | 1118 | 5225 |  | 1
1100110API Grade X65 | 1100 | 110 | API Grade X65 | 10.1636 | 1097.6727 | 1118 | 5595 |  | 1
1100100API Grade X65 | 1100 | 100 | API Grade X65 | 11.18 | 1095.64 | 1118 | 6000 |  | 1
1200160API Grade X65 | 1200 | 160 | API Grade X65 | 7.6188 | 1203.7625 | 1219 | 4892 |  | 1
1200150API Grade X65 | 1200 | 150 | API Grade X65 | 8.1267 | 1202.7467 | 1219 | 5117 |  | 1
1200140API Grade X65 | 1200 | 140 | API Grade X65 | 8.7071 | 1201.5857 | 1219 | 5382 |  | 1
1200130API Grade X65 | 1200 | 130 | API Grade X65 | 9.3769 | 1200.2462 | 1219 | 5731 |  | 1
1200120API Grade X65 | 1200 | 120 | API Grade X65 | 10.1583 | 1198.6833 | 1219 | 6092 |  | 1
1200110API Grade X65 | 1200 | 110 | API Grade X65 | 11.0818 | 1196.8364 | 1219 | 6601 |  | 1
1200100API Grade X65 | 1200 | 100 | API Grade X65 | 12.19 | 1194.62 | 1219 | 7104 |  | 1
1300160API Grade X65 | 1300 | 160 | API Grade X65 | 8.2562 | 1304.4875 | 1321 | 5620 |  | 1
1300150API Grade X65 | 1300 | 150 | API Grade X65 | 8.8067 | 1303.3867 | 1321 | 5890 |  | 1
1300140API Grade X65 | 1300 | 140 | API Grade X65 | 9.4357 | 1302.1286 | 1321 | 6210 |  | 1
1300130API Grade X65 | 1300 | 130 | API Grade X65 | 10.1615 | 1300.6769 | 1321 | 6602 |  | 1
1300120API Grade X65 | 1300 | 120 | API Grade X65 | 11.0083 | 1298.9833 | 1321 | 6985 |  | 1
1300110API Grade X65 | 1300 | 110 | API Grade X65 | 12.0091 | 1296.9818 | 1321 | 7523 |  | 1
1300100API Grade X65 | 1300 | 100 | API Grade X65 | 13.21 | 1294.58 | 1321 | 8025 |  | 1
1400160API Grade X65 | 1400 | 160 | API Grade X65 | 8.8875 | 1404.225 | 1422 | 6345 |  | 1
1400150API Grade X65 | 1400 | 150 | API Grade X65 | 9.48 | 1403.04 | 1422 | 6671 |  | 1
1400140API Grade X65 | 1400 | 140 | API Grade X65 | 10.1571 | 1401.6857 | 1422 | 7058 |  | 1
1400130API Grade X65 | 1400 | 130 | API Grade X65 | 10.9385 | 1400.1231 | 1422 | 7438 |  | 1
1400120API Grade X65 | 1400 | 120 | API Grade X65 | 11.85 | 1398.3 | 1422 | 7998 |  | 1
1400110API Grade X65 | 1400 | 110 | API Grade X65 | 12.9273 | 1396.1455 | 1422 | 8589 |  | 1
1400100API Grade X65 | 1400 | 100 | API Grade X65 | 14.22 | 1393.56 | 1422 | 9350 |  | 1
1500160API Grade X65 | 1500 | 160 | API Grade X65 | 9.525 | 1504.95 | 1524 | 7172 |  | 1
1500150API Grade X65 | 1500 | 150 | API Grade X65 | 10.16 | 1503.68 | 1524 | 7583 |  | 1
1500140API Grade X65 | 1500 | 140 | API Grade X65 | 10.8857 | 1502.2286 | 1524 | 8055 |  | 1
1500130API Grade X65 | 1500 | 130 | API Grade X65 | 11.7231 | 1500.5538 | 1524 | 8510 |  | 1
1500120API Grade X65 | 1500 | 120 | API Grade X65 | 12.7 | 1498.6 | 1524 | 9109 |  | 1
1500110API Grade X65 | 1500 | 110 | API Grade X65 | 13.8545 | 1496.2909 | 1524 | 9907 |  | 1
1500100API Grade X65 | 1500 | 100 | API Grade X65 | 15.24 | 1493.52 | 1524 | 10861 |  | 1
1600160API Grade X65 | 1600 | 160 | API Grade X65 | 10.1625 | 1605.675 | 1626 | 8194 |  | 1
1600150API Grade X65 | 1600 | 150 | API Grade X65 | 10.84 | 1604.32 | 1626 | 8608 |  | 1
1600140API Grade X65 | 1600 | 140 | API Grade X65 | 11.6143 | 1602.7714 | 1626 | 9154 |  | 1
1600130API Grade X65 | 1600 | 130 | API Grade X65 | 12.5077 | 1600.9846 | 1626 | 9711 |  | 1
1600120API Grade X65 | 1600 | 120 | API Grade X65 | 13.55 | 1598.9 | 1626 | 10456 |  | 1
1600110API Grade X65 | 1600 | 110 | API Grade X65 | 14.7818 | 1596.4364 | 1626 | 11254 |  | 1
1700160API Grade X65 | 1700 | 160 | API Grade X65 | 10.7937 | 1705.4125 | 1727 | 9087 |  | 1
1700150API Grade X65 | 1700 | 150 | API Grade X65 | 11.5133 | 1703.9733 | 1727 | 9561 |  | 1
1700140API Grade X65 | 1700 | 140 | API Grade X65 | 12.3357 | 1702.3286 | 1727 | 10129 |  | 1
1700130API Grade X65 | 1700 | 130 | API Grade X65 | 13.2846 | 1700.4308 | 1727 | 10802 |  | 1
1700120API Grade X65 | 1700 | 120 | API Grade X65 | 14.3917 | 1698.2167 | 1727 | 11632 |  | 1
1800160API Grade X65 | 1800 | 160 | API Grade X65 | 11.4313 | 1806.1375 | 1829 | 10355 |  | 1
1800150API Grade X65 | 1800 | 150 | API Grade X65 | 12.1933 | 1804.6133 | 1829 | 10954 |  | 1
1800140API Grade X65 | 1800 | 140 | API Grade X65 | 13.0643 | 1802.8714 | 1829 | 11598 |  | 1
1800130API Grade X65 | 1800 | 130 | API Grade X65 | 14.0692 | 1800.8615 | 1829 | 12405 |  | 1
1800120API Grade X65 | 1800 | 120 | API Grade X65 | 15.2417 | 1798.5167 | 1829 | 13207 |  | 1
1900160API Grade X65 | 1900 | 160 | API Grade X65 | 12.0625 | 1905.875 | 1930 | 11470 |  | 1
1900150API Grade X65 | 1900 | 150 | API Grade X65 | 12.8667 | 1904.2667 | 1930 | 12165 |  | 1
1900140API Grade X65 | 1900 | 140 | API Grade X65 | 13.7857 | 1902.4286 | 1930 | 12915 |  | 1
1900130API Grade X65 | 1900 | 130 | API Grade X65 | 14.8462 | 1900.3077 | 1930 | 13395 |  | 1
2000160API Grade X65 | 2000 | 160 | API Grade X65 | 12.7 | 2006.6 | 2032 | 12464 |  | 1
2000150API Grade X65 | 2000 | 150 | API Grade X65 | 13.5467 | 2004.9067 | 2032 | 13141 |  | 1
2000140API Grade X65 | 2000 | 140 | API Grade X65 | 14.5143 | 2002.9714 | 2032 | 14067 |  | 1
2100160API Grade X65 | 2100 | 160 | API Grade X65 | 13.3375 | 2107.325 | 2134 | 13640 |  | 1
2100150API Grade X65 | 2100 | 150 | API Grade X65 | 14.2267 | 2105.5467 | 2134 | 14556 |  | 1
2100140API Grade X65 | 2100 | 140 | API Grade X65 | 15.2429 | 2103.5143 | 2134 | 15454 |  | 1
2200160API Grade X65 | 2200 | 160 | API Grade X65 | 13.975 | 2208.05 | 2236 | 15253 |  | 1
2200150API Grade X65 | 2200 | 150 | API Grade X65 | 14.9067 | 2206.1867 | 2236 | 16107 |  | 1
2300160API Grade X65 | 2300 | 160 | API Grade X65 | 14.6062 | 2307.7875 | 2337 | 16388 |  | 1
2400160API Grade X65 | 2400 | 160 | API Grade X65 | 15.3125 | 2419.375 | 2450 | 17905 |  | 1
328
Lookup Table
Copy & paste special summary table. Sort Ascending | [6 empty] | 1
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Unique Code | ND | D/t | Grading | wt | ID | OD | Price (R/m) Delivered
1000100API Grade X42 | 1000 | 100 | API Grade X42 | 10.16 | 995.68 | 1016 | 4825
1000100API Grade X52 | 1000 | 100 | API Grade X52 | 10.16 | 995.68 | 1016 | 4898
1000100API Grade X65 | 1000 | 100 | API Grade X65 | 10.16 | 995.68 | 1016 | 5067
1000110API Grade X42 | 1000 | 110 | API Grade X42 | 9.2364 | 997.5273 | 1016 | 4475 | [8 empty] | Unique Code | ND | D/t | Grading | wt | ID | OD | Price (R/m) Delivered
1000110API Grade X52 | 1000 | 110 | API Grade X52 | 9.2364 | 997.5273 | 1016 | 4541 | [8 empty] | 700100API Grade X42 | 700 | 100 | API Grade X42 | 7.11 | 696.78 | 711 | 2586
1000110API Grade X65 | 1000 | 110 | API Grade X65 | 9.2364 | 997.5273 | 1016 | 4694 | [8 empty] | 800100API Grade X42 | 800 | 100 | API Grade X42 | 8.13 | 796.74 | 813 | 3226
1000120API Grade X42 | 1000 | 120 | API Grade X42 | 8.4667 | 999.0667 | 1016 | 4214 | [8 empty] | 900100API Grade X42 | 900 | 100 | API Grade X42 | 9.14 | 895.72 | 914 | 3938
1000120API Grade X52 | 1000 | 120 | API Grade X52 | 8.4667 | 999.0667 | 1016 | 4275 | [8 empty] | 1000100API Grade X42 | 1000 | 100 | API Grade X42 | 10.16 | 995.68 | 1016 | 4825
1000120API Grade X65 | 1000 | 120 | API Grade X65 | 8.4667 | 999.0667 | 1016 | 4416 | [8 empty] | 1100100API Grade X42 | 1100 | 100 | API Grade X42 | 11.18 | 1095.64 | 1118 | 5707
1000130API Grade X42 | 1000 | 130 | API Grade X42 | 7.8154 | 1000.3692 | 1016 | 3969 | [8 empty] | 1200100API Grade X42 | 1200 | 100 | API Grade X42 | 12.19 | 1194.62 | 1219 | 6757
1000130API Grade X52 | 1000 | 130 | API Grade X52 | 7.8154 | 1000.3692 | 1016 | 4026 | [8 empty] | 1300100API Grade X42 | 1300 | 100 | API Grade X42 | 13.21 | 1294.58 | 1321 | 7624
1000130API Grade X65 | 1000 | 130 | API Grade X65 | 7.8154 | 1000.3692 | 1016 | 4155 | [8 empty] | 1400100API Grade X42 | 1400 | 100 | API Grade X42 | 14.22 | 1393.56 | 1422 | 8880
1000140API Grade X42 | 1000 | 140 | API Grade X42 | 7.2571 | 1001.4857 | 1016 | 3798 | [8 empty] | 1500100API Grade X42 | 1500 | 100 | API Grade X42 | 15.24 | 1493.52 | 1524 | 10320
1000140API Grade X52 | 1000 | 140 | API Grade X52 | 7.2571 | 1001.4857 | 1016 | 3850 | [8 empty] | 1600100API Grade X42 | 1600 | 100 | API Grade X42 | 16.26 | 1593.48 | 1626 | 11670
1000140API Grade X65 | 1000 | 140 | API Grade X65 | 7.2571 | 1001.4857 | 1016 | 3971 | [8 empty] | 1700100API Grade X42 | 1700 | 100 | API Grade X42 | 17.27 | 1692.46 | 1727 | 13121
1000150API Grade X42 | 1000 | 150 | API Grade X42 | 6.7733 | 1002.4533 | 1016 | 3625 | [8 empty] | 1800100API Grade X42 | 1800 | 100 | API Grade X42 | 18.29 | 1792.42 | 1829 | 14932
1000150API Grade X52 | 1000 | 150 | API Grade X52 | 6.7733 | 1002.4533 | 1016 | 3675 | [8 empty] | 1900100API Grade X42 | 1900 | 100 | API Grade X42 | 19.3 | 1891.4 | 1930 | 16308
1000150API Grade X65 | 1000 | 150 | API Grade X65 | 6.7733 | 1002.4533 | 1016 | 3787 | [8 empty] | 2000100API Grade X42 | 2000 | 100 | API Grade X42 | 20.32 | 1991.36 | 2032 | 17951
1000160API Grade X42 | 1000 | 160 | API Grade X42 | 6.35 | 1003.3 | 1016 | 3488 | [8 empty] | 2100100API Grade X42 | 2100 | 100 | API Grade X42 | 21.34 | 2091.32 | 2134 | 19475
1000160API Grade X52 | 1000 | 160 | API Grade X52 | 6.35 | 1003.3 | 1016 | 3533 | [8 empty] | 700110API Grade X42 | 700 | 110 | API Grade X42 | 6.4636 | 698.0727 | 711 | 2434
1000160API Grade X65 | 1000 | 160 | API Grade X65 | 6.35 | 1003.3 | 1016 | 3640 | [8 empty] | 800110API Grade X42 | 800 | 110 | API Grade X42 | 7.3909 | 798.2182 | 813 | 3031
1100100API Grade X42 | 1100 | 100 | API Grade X42 | 11.18 | 1095.64 | 1118 | 5707 | [8 empty] | 900110API Grade X42 | 900 | 110 | API Grade X42 | 8.3091 | 897.3818 | 914 | 3692
1100100API Grade X52 | 1100 | 100 | API Grade X52 | 11.18 | 1095.64 | 1118 | 5795 | [8 empty] | 1000110API Grade X42 | 1000 | 110 | API Grade X42 | 9.2364 | 997.5273 | 1016 | 4475
1100100API Grade X65 | 1100 | 100 | API Grade X65 | 11.18 | 1095.64 | 1118 | 6000 | [8 empty] | 1100110API Grade X42 | 1100 | 110 | API Grade X42 | 10.1636 | 1097.6727 | 1118 | 5329
1100110API Grade X42 | 1100 | 110 | API Grade X42 | 10.1636 | 1097.6727 | 1118 | 5329 | [8 empty] | 1200110API Grade X42 | 1200 | 110 | API Grade X42 | 11.0818 | 1196.8364 | 1219 | 6284
1100110API Grade X52 | 1100 | 110 | API Grade X52 | 10.1636 | 1097.6727 | 1118 | 5410 | [8 empty] | 1300110API Grade X42 | 1300 | 110 | API Grade X42 | 12.0091 | 1296.9818 | 1321 | 7152
1100110API Grade X65 | 1100 | 110 | API Grade X65 | 10.1636 | 1097.6727 | 1118 | 5595 | [8 empty] | 1400110API Grade X42 | 1400 | 110 | API Grade X42 | 12.9273 | 1396.1455 | 1422 | 8160
1100120API Grade X42 | 1100 | 120 | API Grade X42 | 9.3167 | 1099.3667 | 1118 | 4981 | [8 empty] | 1500110API Grade X42 | 1500 | 110 | API Grade X42 | 13.8545 | 1496.2909 | 1524 | 9411
1100120API Grade X52 | 1100 | 120 | API Grade X52 | 9.3167 | 1099.3667 | 1118 | 5055 | [8 empty] | 1600110API Grade X42 | 1600 | 110 | API Grade X42 | 14.7818 | 1596.4364 | 1626 | 10691
1100120API Grade X65 | 1100 | 120 | API Grade X65 | 9.3167 | 1099.3667 | 1118 | 5225 | [8 empty] | 1700110API Grade X42 | 1700 | 110 | API Grade X42 | 15.7 | 1695.6 | 1727 | 11965
1100130API Grade X42 | 1100 | 130 | API Grade X42 | 8.6 | 1100.8 | 1118 | 4705 | [8 empty] | 1800110API Grade X42 | 1800 | 110 | API Grade X42 | 16.6273 | 1795.7455 | 1829 | 13607
1100130API Grade X52 | 1100 | 130 | API Grade X52 | 8.6 | 1100.8 | 1118 | 4773 | [8 empty] | 1900110API Grade X42 | 1900 | 110 | API Grade X42 | 17.5455 | 1894.9091 | 1930 | 14977
1100130API Grade X65 | 1100 | 130 | API Grade X65 | 8.6 | 1100.8 | 1118 | 4930 | [8 empty] | 2000110API Grade X42 | 2000 | 110 | API Grade X42 | 18.4727 | 1995.0545 | 2032 | 16516
1100140API Grade X42 | 1100 | 140 | API Grade X42 | 7.9857 | 1102.0286 | 1118 | 4478 | [8 empty] | 2100110API Grade X42 | 2100 | 110 | API Grade X42 | 19.4 | 2095.2 | 2134 | 17993
1100140API Grade X52 | 1100 | 140 | API Grade X52 | 7.9857 | 1102.0286 | 1118 | 4541 | [8 empty] | 2200110API Grade X42 | 2200 | 110 | API Grade X42 | 20.3273 | 2195.3455 | 2236 | 20179
1100140API Grade X65 | 1100 | 140 | API Grade X65 | 7.9857 | 1102.0286 | 1118 | 4687 | [8 empty] | 2300110API Grade X42 | 2300 | 110 | API Grade X42 | 21.2455 | 2294.5091 | 2337 | 21465
1100150API Grade X42 | 1100 | 150 | API Grade X42 | 7.4533 | 1103.0933 | 1118 | 4284 | [8 empty] | 700120API Grade X42 | 700 | 120 | API Grade X42 | 5.925 | 699.15 | 711 | 2290
1100150API Grade X52 | 1100 | 150 | API Grade X52 | 7.4533 | 1103.0933 | 1118 | 4343 | [8 empty] | 800120API Grade X42 | 800 | 120 | API Grade X42 | 6.775 | 799.45 | 813 | 2867
1100150API Grade X65 | 1100 | 150 | API Grade X65 | 7.4533 | 1103.0933 | 1118 | 4480 | [8 empty] | 900120API Grade X42 | 900 | 120 | API Grade X42 | 7.6167 | 898.7667 | 914 | 3473
1100160API Grade X42 | 1100 | 160 | API Grade X42 | 6.9875 | 1104.025 | 1118 | 4094 | [8 empty] | 1000120API Grade X42 | 1000 | 120 | API Grade X42 | 8.4667 | 999.0667 | 1016 | 4214
1100160API Grade X52 | 1100 | 160 | API Grade X52 | 6.9875 | 1104.025 | 1118 | 4150 | [8 empty] | 1100120API Grade X42 | 1100 | 120 | API Grade X42 | 9.3167 | 1099.3667 | 1118 | 4981
1100160API Grade X65 | 1100 | 160 | API Grade X65 | 6.9875 | 1104.025 | 1118 | 4278 | [8 empty] | 1200120API Grade X42 | 1200 | 120 | API Grade X42 | 10.1583 | 1198.6833 | 1219 | 5800
1200100API Grade X42 | 1200 | 100 | API Grade X42 | 12.19 | 1194.62 | 1219 | 6757 | [8 empty] | 1300120API Grade X42 | 1300 | 120 | API Grade X42 | 11.0083 | 1298.9833 | 1321 | 6745
1200100API Grade X52 | 1200 | 100 | API Grade X52 | 12.19 | 1194.62 | 1219 | 6862 | [8 empty] | 1400120API Grade X42 | 1400 | 120 | API Grade X42 | 11.85 | 1398.3 | 1422 | 7602
1200100API Grade X65 | 1200 | 100 | API Grade X65 | 12.19 | 1194.62 | 1219 | 7104 | [8 empty] | 1500120API Grade X42 | 1500 | 120 | API Grade X42 | 12.7 | 1498.6 | 1524 | 8631
1200110API Grade X42 | 1200 | 110 | API Grade X42 | 11.0818 | 1196.8364 | 1219 | 6284 | [8 empty] | 1600120API Grade X42 | 1600 | 120 | API Grade X42 | 13.55 | 1598.9 | 1626 | 9938
1200110API Grade X52 | 1200 | 110 | API Grade X52 | 11.0818 | 1196.8364 | 1219 | 6380 | [8 empty] | 1700120API Grade X42 | 1700 | 120 | API Grade X42 | 14.3917 | 1698.2167 | 1727 | 11051
1200110API Grade X65 | 1200 | 110 | API Grade X65 | 11.0818 | 1196.8364 | 1219 | 6601 | [8 empty] | 1800120API Grade X42 | 1800 | 120 | API Grade X42 | 15.2417 | 1798.5167 | 1829 | 12557
1200120API Grade X42 | 1200 | 120 | API Grade X42 | 10.1583 | 1198.6833 | 1219 | 5800 | [8 empty] | 1900120API Grade X42 | 1900 | 120 | API Grade X42 | 16.0833 | 1897.8333 | 1930 | 13938
1200120API Grade X52 | 1200 | 120 | API Grade X52 | 10.1583 | 1198.6833 | 1219 | 5888 | [8 empty] | 2000120API Grade X42 | 2000 | 120 | API Grade X42 | 16.9333 | 1998.1333 | 2032 | 15141
1200120API Grade X65 | 1200 | 120 | API Grade X65 | 10.1583 | 1198.6833 | 1219 | 6092 | [8 empty] | 2100120API Grade X42 | 2100 | 120 | API Grade X42 | 17.7833 | 2098.4333 | 2134 | 16739
1200130API Grade X42 | 1200 | 130 | API Grade X42 | 9.3769 | 1200.2462 | 1219 | 5463 | [8 empty] | 2200120API Grade X42 | 2200 | 120 | API Grade X42 | 18.6333 | 2198.7333 | 2236 | 18441
1200130API Grade X52 | 1200 | 130 | API Grade X52 | 9.3769 | 1200.2462 | 1219 | 5543 | [8 empty] | 2300120API Grade X42 | 2300 | 120 | API Grade X42 | 19.475 | 2298.05 | 2337 | 19949
1200130API Grade X65 | 1200 | 130 | API Grade X65 | 9.3769 | 1200.2462 | 1219 | 5731 | [8 empty] | 2400120API Grade X42 | 2400 | 120 | API Grade X42 | 20.4167 | 2409.1667 | 2450 | 21714
1200140API Grade X42 | 1200 | 140 | API Grade X42 | 8.7071 | 1201.5857 | 1219 | 5134 | [8 empty] | 2500120API Grade X42 | 2500 | 120 | API Grade X42 | 21.1667 | 2497.6667 | 2540 | 23308
1200140API Grade X52 | 1200 | 140 | API Grade X52 | 8.7071 | 1201.5857 | 1219 | 5209 | [8 empty] | 700130API Grade X42 | 700 | 130 | API Grade X42 | 5.4692 | 700.0615 | 711 | 2194
1200140API Grade X65 | 1200 | 140 | API Grade X65 | 8.7071 | 1201.5857 | 1219 | 5382 | [8 empty] | 800130API Grade X42 | 800 | 130 | API Grade X42 | 6.2538 | 800.4923 | 813 | 2730
1200150API Grade X42 | 1200 | 150 | API Grade X42 | 8.1267 | 1202.7467 | 1219 | 4886 | [8 empty] | 900130API Grade X42 | 900 | 130 | API Grade X42 | 7.0308 | 899.9385 | 914 | 3279
1200150API Grade X52 | 1200 | 150 | API Grade X52 | 8.1267 | 1202.7467 | 1219 | 4955 | [8 empty] | 1000130API Grade X42 | 1000 | 130 | API Grade X42 | 7.8154 | 1000.3692 | 1016 | 3969
1200150API Grade X65 | 1200 | 150 | API Grade X65 | 8.1267 | 1202.7467 | 1219 | 5117 | [8 empty] | 1100130API Grade X42 | 1100 | 130 | API Grade X42 | 8.6 | 1100.8 | 1118 | 4705
1200160API Grade X42 | 1200 | 160 | API Grade X42 | 7.6188 | 1203.7625 | 1219 | 4675 | [8 empty] | 1200130API Grade X42 | 1200 | 130 | API Grade X42 | 9.3769 | 1200.2462 | 1219 | 5463
1200160API Grade X52 | 1200 | 160 | API Grade X52 | 7.6188 | 1203.7625 | 1219 | 4740 | [8 empty] | 1300130API Grade X42 | 1300 | 130 | API Grade X42 | 10.1615 | 1300.6769 | 1321 | 6286
1200160API Grade X65 | 1200 | 160 | API Grade X65 | 7.6188 | 1203.7625 | 1219 | 4892 | [8 empty] | 1400130API Grade X42 | 1400 | 130 | API Grade X42 | 10.9385 | 1400.1231 | 1422 | 7076
1300100API Grade X42 | 1300 | 100 | API Grade X42 | 13.21 | 1294.58 | 1321 | 7624 | [8 empty] | 1500130API Grade X42 | 1500 | 130 | API Grade X42 | 11.7231 | 1500.5538 | 1524 | 8013
1300100API Grade X52 | 1300 | 100 | API Grade X52 | 13.21 | 1294.58 | 1321 | 7745 | [8 empty] | 1600130API Grade X42 | 1600 | 130 | API Grade X42 | 12.5077 | 1600.9846 | 1626 | 9235
1300100API Grade X65 | 1300 | 100 | API Grade X65 | 13.21 | 1294.58 | 1321 | 8025 | [8 empty] | 1700130API Grade X42 | 1700 | 130 | API Grade X42 | 13.2846 | 1700.4308 | 1727 | 10264
1300110API Grade X42 | 1300 | 110 | API Grade X42 | 12.0091 | 1296.9818 | 1321 | 7152 | [8 empty] | 1800130API Grade X42 | 1800 | 130 | API Grade X42 | 14.0692 | 1800.8615 | 1829 | 11801
1300110API Grade X52 | 1300 | 110 | API Grade X52 | 12.0091 | 1296.9818 | 1321 | 7265 | [8 empty] | 1900130API Grade X42 | 1900 | 130 | API Grade X42 | 14.8462 | 1900.3077 | 1930 | 12727
1300110API Grade X65 | 1300 | 110 | API Grade X65 | 12.0091 | 1296.9818 | 1321 | 7523 | [8 empty] | 2000130API Grade X42 | 2000 | 130 | API Grade X42 | 15.6308 | 2000.7385 | 2032 | 14238
1300120API Grade X42 | 1300 | 120 | API Grade X42 | 11.0083 | 1298.9833 | 1321 | 6745 | [8 empty] | 2100130API Grade X42 | 2100 | 130 | API Grade X42 | 16.4154 | 2101.1692 | 2134 | 15509
1300120API Grade X52 | 1300 | 120 | API Grade X52 | 11.0083 | 1298.9833 | 1321 | 6747 | [8 empty] | 2200130API Grade X42 | 2200 | 130 | API Grade X42 | 17.2 | 2201.6 | 2236 | 17484
1300120API Grade X65 | 1300 | 120 | API Grade X65 | 11.0083 | 1298.9833 | 1321 | 6985 | [8 empty] | 2300130API Grade X42 | 2300 | 130 | API Grade X42 | 17.9769 | 2301.0462 | 2337 | 18615
1300130API Grade X42 | 1300 | 130 | API Grade X42 | 10.1615 | 1300.6769 | 1321 | 6286 | [8 empty] | 2400130API Grade X42 | 2400 | 130 | API Grade X42 | 18.8462 | 2412.3077 | 2450 | 20567
1300130API Grade X52 | 1300 | 130 | API Grade X52 | 10.1615 | 1300.6769 | 1321 | 6381 | [8 empty] | 2500130API Grade X42 | 2500 | 130 | API Grade X42 | 19.5385 | 2500.9231 | 2540 | 21639
1300130API Grade X65 | 1300 | 130 | API Grade X65 | 10.1615 | 1300.6769 | 1321 | 6602 | [8 empty] | 700140API Grade X42 | 700 | 140 | API Grade X42 | 5.0786 | 700.8429 | 711 | 2098
1300140API Grade X42 | 1300 | 140 | API Grade X42 | 9.4357 | 1302.1286 | 1321 | 5920 | [8 empty] | 800140API Grade X42 | 800 | 140 | API Grade X42 | 5.8071 | 801.3857 | 813 | 2592
1300140API Grade X52 | 1300 | 140 | API Grade X52 | 9.4357 | 1302.1286 | 1321 | 6007 | [8 empty] | 900140API Grade X42 | 900 | 140 | API Grade X42 | 6.5286 | 900.9429 | 914 | 3125
1300140API Grade X65 | 1300 | 140 | API Grade X65 | 9.4357 | 1302.1286 | 1321 | 6210 | [8 empty] | 1000140API Grade X42 | 1000 | 140 | API Grade X42 | 7.2571 | 1001.4857 | 1016 | 3798
1300150API Grade X42 | 1300 | 150 | API Grade X42 | 8.8067 | 1303.3867 | 1321 | 5617 | [8 empty] | 1100140API Grade X42 | 1100 | 140 | API Grade X42 | 7.9857 | 1102.0286 | 1118 | 4478
1300150API Grade X52 | 1300 | 150 | API Grade X52 | 8.8067 | 1303.3867 | 1321 | 5699 | [8 empty] | 1200140API Grade X42 | 1200 | 140 | API Grade X42 | 8.7071 | 1201.5857 | 1219 | 5134
1300150API Grade X65 | 1300 | 150 | API Grade X65 | 8.8067 | 1303.3867 | 1321 | 5890 | [8 empty] | 1300140API Grade X42 | 1300 | 140 | API Grade X42 | 9.4357 | 1302.1286 | 1321 | 5920
1300160API Grade X42 | 1300 | 160 | API Grade X42 | 8.2562 | 1304.4875 | 1321 | 5363 | [8 empty] | 1400140API Grade X42 | 1400 | 140 | API Grade X42 | 10.1571 | 1401.6857 | 1422 | 6719
1300160API Grade X52 | 1300 | 160 | API Grade X52 | 8.2562 | 1304.4875 | 1321 | 5440 | [8 empty] | 1500140API Grade X42 | 1500 | 140 | API Grade X42 | 10.8857 | 1502.2286 | 1524 | 7665
1300160API Grade X65 | 1300 | 160 | API Grade X65 | 8.2562 | 1304.4875 | 1321 | 5620 | [8 empty] | 1600140API Grade X42 | 1600 | 140 | API Grade X42 | 11.6143 | 1602.7714 | 1626 | 8713
1400100API Grade X42 | 1400 | 100 | API Grade X42 | 14.22 | 1393.56 | 1422 | 8880 | [8 empty] | 1700140API Grade X42 | 1700 | 140 | API Grade X42 | 12.3357 | 1702.3286 | 1727 | 9631
1400100API Grade X52 | 1400 | 100 | API Grade X52 | 14.22 | 1393.56 | 1422 | 9022 | [8 empty] | 1800140API Grade X42 | 1800 | 140 | API Grade X42 | 13.0643 | 1802.8714 | 1829 | 11037
1400100API Grade X65 | 1400 | 100 | API Grade X65 | 14.22 | 1393.56 | 1422 | 9350 | [8 empty] | 1900140API Grade X42 | 1900 | 140 | API Grade X42 | 13.7857 | 1902.4286 | 1930 | 12290
1400110API Grade X42 | 1400 | 110 | API Grade X42 | 12.9273 | 1396.1455 | 1422 | 8160 | [8 empty] | 2000140API Grade X42 | 2000 | 140 | API Grade X42 | 14.5143 | 2002.9714 | 2032 | 13377
1400110API Grade X52 | 1400 | 110 | API Grade X52 | 12.9273 | 1396.1455 | 1422 | 8290 | [8 empty] | 2100140API Grade X42 | 2100 | 140 | API Grade X42 | 15.2429 | 2103.5143 | 2134 | 14695
1400110API Grade X65 | 1400 | 110 | API Grade X65 | 12.9273 | 1396.1455 | 1422 | 8589 | [8 empty] | 2200140API Grade X42 | 2200 | 140 | API Grade X42 | 15.9714 | 2204.0571 | 2236 | 16300
1400120API Grade X42 | 1400 | 120 | API Grade X42 | 11.85 | 1398.3 | 1422 | 7602 | [8 empty] | 2300140API Grade X42 | 2300 | 140 | API Grade X42 | 16.6929 | 2303.6143 | 2337 | 17459
1400120API Grade X52 | 1400 | 120 | API Grade X52 | 11.85 | 1398.3 | 1422 | 7722 | [8 empty] | 2400140API Grade X42 | 2400 | 140 | API Grade X42 | 17.5 | 2415 | 2450 | 18988
1400120API Grade X65 | 1400 | 120 | API Grade X65 | 11.85 | 1398.3 | 1422 | 7998 | [8 empty] | 2500140API Grade X42 | 2500 | 140 | API Grade X42 | 18.1429 | 2503.7143 | 2540 | 20262
1400130API Grade X42 | 1400 | 130 | API Grade X42 | 10.9385 | 1400.1231 | 1422 | 7076 | [8 empty] | 800150API Grade X42 | 800 | 150 | API Grade X42 | 5.42 | 802.16 | 813 | 2483
1400130API Grade X52 | 1400 | 130 | API Grade X52 | 10.9385 | 1400.1231 | 1422 | 7185 | [8 empty] | 900150API Grade X42 | 900 | 150 | API Grade X42 | 6.0933 | 901.8133 | 914 | 3002
1400130API Grade X65 | 1400 | 130 | API Grade X65 | 10.9385 | 1400.1231 | 1422 | 7438 | [8 empty] | 1000150API Grade X42 | 1000 | 150 | API Grade X42 | 6.7733 | 1002.4533 | 1016 | 3625
1400140API Grade X42 | 1400 | 140 | API Grade X42 | 10.1571 | 1401.6857 | 1422 | 6719 | [8 empty] | 1100150API Grade X42 | 1100 | 150 | API Grade X42 | 7.4533 | 1103.0933 | 1118 | 4284
1400140API Grade X52 | 1400 | 140 | API Grade X52 | 10.1571 | 1401.6857 | 1422 | 6821 | [8 empty] | 1200150API Grade X42 | 1200 | 150 | API Grade X42 | 8.1267 | 1202.7467 | 1219 | 4886
1400140API Grade X65 | 1400 | 140 | API Grade X65 | 10.1571 | 1401.6857 | 1422 | 7058 | [8 empty] | 1300150API Grade X42 | 1300 | 150 | API Grade X42 | 8.8067 | 1303.3867 | 1321 | 5617
1400150API Grade X42 | 1400 | 150 | API Grade X42 | 9.48 | 1403.04 | 1422 | 6354 | [8 empty] | 1400150API Grade X42 | 1400 | 150 | API Grade X42 | 9.48 | 1403.04 | 1422 | 6354
1400150API Grade X52 | 1400 | 150 | API Grade X52 | 9.48 | 1403.04 | 1422 | 6450 | [8 empty] | 1500150API Grade X42 | 1500 | 150 | API Grade X42 | 10.16 | 1503.68 | 1524 | 7209
1400150API Grade X65 | 1400 | 150 | API Grade X65 | 9.48 | 1403.04 | 1422 | 6671 | [8 empty] | 1600150API Grade X42 | 1600 | 150 | API Grade X42 | 10.84 | 1604.32 | 1626 | 8196
1400160API Grade X42 | 1400 | 160 | API Grade X42 | 8.8875 | 1404.225 | 1422 | 6048 | [8 empty] | 1700150API Grade X42 | 1700 | 150 | API Grade X42 | 11.5133 | 1703.9733 | 1727 | 9096
1400160API Grade X52 | 1400 | 160 | API Grade X52 | 8.8875 | 1404.225 | 1422 | 6140 | [8 empty] | 1800150API Grade X42 | 1800 | 150 | API Grade X42 | 12.1933 | 1804.6133 | 1829 | 10431
1400160API Grade X65 | 1400 | 160 | API Grade X65 | 8.8875 | 1404.225 | 1422 | 6345 | [8 empty] | 1900150API Grade X42 | 1900 | 150 | API Grade X42 | 12.8667 | 1904.2667 | 1930 | 11581
1500100API Grade X42 | 1500 | 100 | API Grade X42 | 15.24 | 1493.52 | 1524 | 10320 | [8 empty] | 2000150API Grade X42 | 2000 | 150 | API Grade X42 | 13.5467 | 2004.9067 | 2032 | 12498
1500100API Grade X52 | 1500 | 100 | API Grade X52 | 15.24 | 1493.52 | 1524 | 10483 | [8 empty] | 2100150API Grade X42 | 2100 | 150 | API Grade X42 | 14.2267 | 2105.5467 | 2134 | 13845
1500100API Grade X65 | 1500 | 100 | API Grade X65 | 15.24 | 1493.52 | 1524 | 10861 | [8 empty] | 2200150API Grade X42 | 2200 | 150 | API Grade X42 | 14.9067 | 2206.1867 | 2236 | 15311
1500110API Grade X42 | 1500 | 110 | API Grade X42 | 13.8545 | 1496.2909 | 1524 | 9411 | [8 empty] | 2300150API Grade X42 | 2300 | 150 | API Grade X42 | 15.58 | 2305.84 | 2337 | 16477
1500110API Grade X52 | 1500 | 110 | API Grade X52 | 13.8545 | 1496.2909 | 1524 | 9561 | [8 empty] | 2400150API Grade X42 | 2400 | 150 | API Grade X42 | 16.3333 | 2417.3333 | 2450 | 17865
1500110API Grade X65 | 1500 | 110 | API Grade X65 | 13.8545 | 1496.2909 | 1524 | 9907 | [8 empty] | 2500150API Grade X42 | 2500 | 150 | API Grade X42 | 16.9333 | 2506.1333 | 2540 | 19082
1500120API Grade X42 | 1500 | 120 | API Grade X42 | 12.7 | 1498.6 | 1524 | 8631 | [8 empty] | 800160API Grade X42 | 800 | 160 | API Grade X42 | 5.0812 | 802.8375 | 813 | 2400
1500120API Grade X52 | 1500 | 120 | API Grade X52 | 12.7 | 1498.6 | 1524 | 8793 | [8 empty] | 900160API Grade X42 | 900 | 160 | API Grade X42 | 5.7125 | 902.575 | 914 | 2878
1500120API Grade X65 | 1500 | 120 | API Grade X65 | 12.7 | 1498.6 | 1524 | 9109 | [8 empty] | 1000160API Grade X42 | 1000 | 160 | API Grade X42 | 6.35 | 1003.3 | 1016 | 3488
1500130API Grade X42 | 1500 | 130 | API Grade X42 | 11.7231 | 1500.5538 | 1524 | 8105 | [8 empty] | 1100160API Grade X42 | 1100 | 160 | API Grade X42 | 6.9875 | 1104.025 | 1118 | 4094
1500130API Grade X52 | 1500 | 130 | API Grade X52 | 11.7231 | 1500.5538 | 1524 | 8219 | [8 empty] | 1200160API Grade X42 | 1200 | 160 | API Grade X42 | 7.6188 | 1203.7625 | 1219 | 4675
1500130API Grade X65 | 1500 | 130 | API Grade X65 | 11.7231 | 1500.5538 | 1524 | 8510 | [8 empty] | 1300160API Grade X42 | 1300 | 160 | API Grade X42 | 8.2562 | 1304.4875 | 1321 | 5363
1500140API Grade X42 | 1500 | 140 | API Grade X42 | 10.8857 | 1502.2286 | 1524 | 7665 | [8 empty] | 1400160API Grade X42 | 1400 | 160 | API Grade X42 | 8.8875 | 1404.225 | 1422 | 6048
1500140API Grade X52 | 1500 | 140 | API Grade X52 | 10.8857 | 1502.2286 | 1524 | 7782 | [8 empty] | 1500160API Grade X42 | 1500 | 160 | API Grade X42 | 9.525 | 1504.95 | 1524 | 6832
1500140API Grade X65 | 1500 | 140 | API Grade X65 | 10.8857 | 1502.2286 | 1524 | 8055 | [8 empty] | 1600160API Grade X42 | 1600 | 160 | API Grade X42 | 10.1625 | 1605.675 | 1626 | 7805
1500150API Grade X42 | 1500 | 150 | API Grade X42 | 10.16 | 1503.68 | 1524 | 7209 | [8 empty] | 1700160API Grade X42 | 1700 | 160 | API Grade X42 | 10.7937 | 1705.4125 | 1727 | 8650
1500150API Grade X52 | 1500 | 150 | API Grade X52 | 10.16 | 1503.68 | 1524 | 7328 | [8 empty] | 1800160API Grade X42 | 1800 | 160 | API Grade X42 | 11.4313 | 1806.1375 | 1829 | 9866
1500150API Grade X65 | 1500 | 150 | API Grade X65 | 10.16 | 1503.68 | 1524 | 7583 | [8 empty] | 1900160API Grade X42 | 1900 | 160 | API Grade X42 | 12.0625 | 1905.875 | 1930 | 10922
1500160API Grade X42 | 1500 | 160 | API Grade X42 | 9.525 | 1504.95 | 1524 | 6832 | [8 empty] | 2000160API Grade X42 | 2000 | 160 | API Grade X42 | 12.7 | 2006.6 | 2032 | 11859
1500160API Grade X52 | 1500 | 160 | API Grade X52 | 9.525 | 1504.95 | 1524 | 6935 | [8 empty] | 2100160API Grade X42 | 2100 | 160 | API Grade X42 | 13.3375 | 2107.325 | 2134 | 12975
1500160API Grade X65 | 1500 | 160 | API Grade X65 | 9.525 | 1504.95 | 1524 | 7172 | [8 empty] | 2200160API Grade X42 | 2200 | 160 | API Grade X42 | 13.975 | 2208.05 | 2236 | 14503
1600100API Grade X42 | 1600 | 100 | API Grade X42 | 16.26 | 1593.48 | 1626 | 11670 | [8 empty] | 2300160API Grade X42 | 2300 | 160 | API Grade X42 | 14.6062 | 2307.7875 | 2337 | 15580
1600110API Grade X42 | 1600 | 110 | API Grade X42 | 14.7818 | 1596.4364 | 1626 | 10691 | [8 empty] | 2400160API Grade X42 | 2400 | 160 | API Grade X42 | 15.3125 | 2419.375 | 2450 | 16924
1600110API Grade X52 | 1600 | 110 | API Grade X52 | 14.7818 | 1596.4364 | 1626 | 10861 | [8 empty] | 2500160API Grade X42 | 2500 | 160 | API Grade X42 | 15.875 | 2508.25 | 2540 | 18095
1600110API Grade X65 | 1600 | 110 | API Grade X65 | 14.7818 | 1596.4364 | 1626 | 11254
1600120API Grade X42 | 1600 | 120 | API Grade X42 | 13.55 | 1598.9 | 1626 | 9938
1600120API Grade X52 | 1600 | 120 | API Grade X52 | 13.55 | 1598.9 | 1626 | 10095
1600120API Grade X65 | 1600 | 120 | API Grade X65 | 13.55 | 1598.9 | 1626 | 10456
1600130API Grade X42 | 1600 | 130 | API Grade X42 | 12.5077 | 1600.9846 | 1626 | 9235
1600130API Grade X52 | 1600 | 130 | API Grade X52 | 12.5077 | 1600.9846 | 1626 | 9379
1600130API Grade X65 | 1600 | 130 | API Grade X65 | 12.5077 | 1600.9846 | 1626 | 9711
1600140API Grade X42 | 1600 | 140 | API Grade X42 | 11.6143 | 1602.7714 | 1626 | 8713
1600140API Grade X52 | 1600 | 140 | API Grade X52 | 11.6143 | 1602.7714 | 1626 | 8845
1600140API Grade X65 | 1600 | 140 | API Grade X65 | 11.6143 | 1602.7714 | 1626 | 9154
1600150API Grade X42 | 1600 | 150 | API Grade X42 | 10.84 | 1604.32 | 1626 | 8196
1600150API Grade X52 | 1600 | 150 | API Grade X52 | 10.84 | 1604.32 | 1626 | 8320
1600150API Grade X65 | 1600 | 150 | API Grade X65 | 10.84 | 1604.32 | 1626 | 8608
1600160API Grade X42 | 1600 | 160 | API Grade X42 | 10.1625 | 1605.675 | 1626 | 7805
1600160API Grade X52 | 1600 | 160 | API Grade X52 | 10.1625 | 1605.675 | 1626 | 7923
1600160API Grade X65 | 1600 | 160 | API Grade X65 | 10.1625 | 1605.675 | 1626 | 8194
1700100API Grade X42 | 1700 | 100 | API Grade X42 | 17.27 | 1692.46 | 1727 | 13121
1700110API Grade X42 | 1700 | 110 | API Grade X42 | 15.7 | 1695.6 | 1727 | 11965
1700120API Grade X42 | 1700 | 120 | API Grade X42 | 14.3917 | 1698.2167 | 1727 | 11051
1700120API Grade X52 | 1700 | 120 | API Grade X52 | 14.3917 | 1698.2167 | 1727 | 11227
1700120API Grade X65 | 1700 | 120 | API Grade X65 | 14.3917 | 1698.2167 | 1727 | 11632
1700130API Grade X42 | 1700 | 130 | API Grade X42 | 13.2846 | 1700.4308 | 1727 | 10264
1700130API Grade X52 | 1700 | 130 | API Grade X52 | 13.2846 | 1700.4308 | 1727 | 10427
1700130API Grade X65 | 1700 | 130 | API Grade X65 | 13.2846 | 1700.4308 | 1727 | 10802
1700140API Grade X42 | 1700 | 140 | API Grade X42 | 12.3357 | 1702.3286 | 1727 | 9631
1700140API Grade X52 | 1700 | 140 | API Grade X52 | 12.3357 | 1702.3286 | 1727 | 9782
1700140API Grade X65 | 1700 | 140 | API Grade X65 | 12.3357 | 1702.3286 | 1727 | 10129
1700150API Grade X42 | 1700 | 150 | API Grade X42 | 11.5133 | 1703.9733 | 1727 | 9096
1700150API Grade X52 | 1700 | 150 | API Grade X52 | 11.5133 | 1703.9733 | 1727 | 9236
1700150API Grade X65 | 1700 | 150 | API Grade X65 | 11.5133 | 1703.9733 | 1727 | 9561
1700160API Grade X42 | 1700 | 160 | API Grade X42 | 10.7937 | 1705.4125 | 1727 | 8650
1700160API Grade X52 | 1700 | 160 | API Grade X52 | 10.7937 | 1705.4125 | 1727 | 8782
1700160API Grade X65 | 1700 | 160 | API Grade X65 | 10.7937 | 1705.4125 | 1727 | 9087
1800100API Grade X42 | 1800 | 100 | API Grade X42 | 18.29 | 1792.42 | 1829 | 14932
1800110API Grade X42 | 1800 | 110 | API Grade X42 | 16.6273 | 1795.7455 | 1829 | 13607
1800120API Grade X42 | 1800 | 120 | API Grade X42 | 15.2417 | 1798.5167 | 1829 | 12557
1800120API Grade X52 | 1800 | 120 | API Grade X52 | 15.2417 | 1798.5167 | 1829 | 12755
1800120API Grade X65 | 1800 | 120 | API Grade X65 | 15.2417 | 1798.5167 | 1829 | 13207
1800130API Grade X42 | 1800 | 130 | API Grade X42 | 14.0692 | 1800.8615 | 1829 | 11801
1800130API Grade X52 | 1800 | 130 | API Grade X52 | 14.0692 | 1800.8615 | 1829 | 11985
1800130API Grade X65 | 1800 | 130 | API Grade X65 | 14.0692 | 1800.8615 | 1829 | 12405
1800140API Grade X42 | 1800 | 140 | API Grade X42 | 13.0643 | 1802.8714 | 1829 | 11037
1800140API Grade X52 | 1800 | 140 | API Grade X52 | 13.0643 | 1802.8714 | 1829 | 11207
1800140API Grade X65 | 1800 | 140 | API Grade X65 | 13.0643 | 1802.8714 | 1829 | 11598
1800150API Grade X42 | 1800 | 150 | API Grade X42 | 12.1933 | 1804.6133 | 1829 | 10431
1800150API Grade X52 | 1800 | 150 | API Grade X52 | 12.1933 | 1804.6133 | 1829 | 10589
1800150API Grade X65 | 1800 | 150 | API Grade X65 | 12.1933 | 1804.6133 | 1829 | 10954
1800160API Grade X42 | 1800 | 160 | API Grade X42 | 11.4313 | 1806.1375 | 1829 | 9866
1800160API Grade X52 | 1800 | 160 | API Grade X52 | 11.4313 | 1806.1375 | 1829 | 10013
1800160API Grade X65 | 1800 | 160 | API Grade X65 | 11.4313 | 1806.1375 | 1829 | 10355
1900100API Grade X42 | 1900 | 100 | API Grade X42 | 19.3 | 1891.4 | 1930 | 16308
1900110API Grade X42 | 1900 | 110 | API Grade X42 | 17.5455 | 1894.9091 | 1930 | 14977
1900120API Grade X42 | 1900 | 120 | API Grade X42 | 16.0833 | 1897.8333 | 1930 | 13938
1900130API Grade X42 | 1900 | 130 | API Grade X42 | 14.8462 | 1900.3077 | 1930 | 12727
1900130API Grade X52 | 1900 | 130 | API Grade X52 | 14.8462 | 1900.3077 | 1930 | 12929
1900130API Grade X65 | 1900 | 130 | API Grade X65 | 14.8462 | 1900.3077 | 1930 | 13395
1900140API Grade X42 | 1900 | 140 | API Grade X42 | 13.7857 | 1902.4286 | 1930 | 12290
1900140API Grade X52 | 1900 | 140 | API Grade X52 | 13.7857 | 1902.4286 | 1930 | 12479
1900140API Grade X65 | 1900 | 140 | API Grade X65 | 13.7857 | 1902.4286 | 1930 | 12915
1900150API Grade X42 | 1900 | 150 | API Grade X42 | 12.8667 | 1904.2667 | 1930 | 11581
1900150API Grade X52 | 1900 | 150 | API Grade X52 | 12.8667 | 1904.2667 | 1930 | 11758
1900150API Grade X65 | 1900 | 150 | API Grade X65 | 12.8667 | 1904.2667 | 1930 | 12165
1900160API Grade X42 | 1900 | 160 | API Grade X42 | 12.0625 | 1905.875 | 1930 | 10922
1900160API Grade X52 | 1900 | 160 | API Grade X52 | 12.0625 | 1905.875 | 1930 | 11088
1900160API Grade X65 | 1900 | 160 | API Grade X65 | 12.0625 | 1905.875 | 1930 | 11470
2000100API Grade X42 | 2000 | 100 | API Grade X42 | 20.32 | 1991.36 | 2032 | 17951
2000110API Grade X42 | 2000 | 110 | API Grade X42 | 18.4727 | 1995.0545 | 2032 | 16516
2000120API Grade X42 | 2000 | 120 | API Grade X42 | 16.9333 | 1998.1333 | 2032 | 15141
2000130API Grade X42 | 2000 | 130 | API Grade X42 | 15.6308 | 2000.7385 | 2032 | 14238
2000140API Grade X42 | 2000 | 140 | API Grade X42 | 14.5143 | 2002.9714 | 2032 | 13377
2000140API Grade X52 | 2000 | 140 | API Grade X52 | 14.5143 | 2002.9714 | 2032 | 13478
2000140API Grade X65 | 2000 | 140 | API Grade X65 | 14.5143 | 2002.9714 | 2032 | 14067
2000150API Grade X42 | 2000 | 150 | API Grade X42 | 13.5467 | 2004.9067 | 2032 | 12498
2000150API Grade X52 | 2000 | 150 | API Grade X52 | 13.5467 | 2004.9067 | 2032 | 12694
2000150API Grade X65 | 2000 | 150 | API Grade X65 | 13.5467 | 2004.9067 | 2032 | 13141
2000160API Grade X42 | 2000 | 160 | API Grade X42 | 12.7 | 2006.6 | 2032 | 11859
2000160API Grade X52 | 2000 | 160 | API Grade X52 | 12.7 | 2006.6 | 2032 | 12042
2000160API Grade X65 | 2000 | 160 | API Grade X65 | 12.7 | 2006.6 | 2032 | 12464
2100100API Grade X42 | 2100 | 100 | API Grade X42 | 21.34 | 2091.32 | 2134 | 19475
2100110API Grade X42 | 2100 | 110 | API Grade X42 | 19.4 | 2095.2 | 2134 | 17993
2100120API Grade X42 | 2100 | 120 | API Grade X42 | 17.7833 | 2098.4333 | 2134 | 16739
2100130API Grade X42 | 2100 | 130 | API Grade X42 | 16.4154 | 2101.1692 | 2134 | 15509
2100140API Grade X42 | 2100 | 140 | API Grade X42 | 15.2429 | 2103.5143 | 2134 | 14695
2100140API Grade X52 | 2100 | 140 | API Grade X52 | 15.2429 | 2103.5143 | 2134 | 14925
2100140API Grade X65 | 2100 | 140 | API Grade X65 | 15.2429 | 2103.5143 | 2134 | 15454
2100150API Grade X42 | 2100 | 150 | API Grade X42 | 14.2267 | 2105.5467 | 2134 | 13845
2100150API Grade X52 | 2100 | 150 | API Grade X52 | 14.2267 | 2105.5467 | 2134 | 14061
2100150API Grade X65 | 2100 | 150 | API Grade X65 | 14.2267 | 2105.5467 | 2134 | 14556
2100160API Grade X42 | 2100 | 160 | API Grade X42 | 13.3375 | 2107.325 | 2134 | 12975
2100160API Grade X52 | 2100 | 160 | API Grade X52 | 13.3375 | 2107.325 | 2134 | 13177
2100160API Grade X65 | 2100 | 160 | API Grade X65 | 13.3375 | 2107.325 | 2134 | 13640
2200110API Grade X42 | 2200 | 110 | API Grade X42 | 20.3273 | 2195.3455 | 2236 | 20179
2200120API Grade X42 | 2200 | 120 | API Grade X42 | 18.6333 | 2198.7333 | 2236 | 18441
2200130API Grade X42 | 2200 | 130 | API Grade X42 | 17.2 | 2201.6 | 2236 | 17484
2200140API Grade X42 | 2200 | 140 | API Grade X42 | 15.9714 | 2204.0571 | 2236 | 16300
2200150API Grade X42 | 2200 | 150 | API Grade X42 | 14.9067 | 2206.1867 | 2236 | 15311
2200150API Grade X52 | 2200 | 150 | API Grade X52 | 14.9067 | 2206.1867 | 2236 | 15552
2200150API Grade X65 | 2200 | 150 | API Grade X65 | 14.9067 | 2206.1867 | 2236 | 16107
2200160API Grade X42 | 2200 | 160 | API Grade X42 | 13.975 | 2208.05 | 2236 | 14503
2200160API Grade X52 | 2200 | 160 | API Grade X52 | 13.975 | 2208.05 | 2236 | 14730
2200160API Grade X65 | 2200 | 160 | API Grade X65 | 13.975 | 2208.05 | 2236 | 15253
2300110API Grade X42 | 2300 | 110 | API Grade X42 | 21.2455 | 2294.5091 | 2337 | 21465
2300120API Grade X42 | 2300 | 120 | API Grade X42 | 19.475 | 2298.05 | 2337 | 19949
2300130API Grade X42 | 2300 | 130 | API Grade X42 | 17.9769 | 2301.0462 | 2337 | 18615
2300140API Grade X42 | 2300 | 140 | API Grade X42 | 16.6929 | 2303.6143 | 2337 | 17459
2300150API Grade X42 | 2300 | 150 | API Grade X42 | 15.58 | 2305.84 | 2337 | 16477
2300160API Grade X42 | 2300 | 160 | API Grade X42 | 14.6062 | 2307.7875 | 2337 | 15580
2300160API Grade X52 | 2300 | 160 | API Grade X52 | 14.6062 | 2307.7875 | 2337 | 15830
2300160API Grade X65 | 2300 | 160 | API Grade X65 | 14.6062 | 2307.7875 | 2337 | 16388
2400120API Grade X42 | 2400 | 120 | API Grade X42 | 20.4167 | 2409.1667 | 2450 | 21714
2400130API Grade X42 | 2400 | 130 | API Grade X42 | 18.8462 | 2412.3077 | 2450 | 20567
2400140API Grade X42 | 2400 | 140 | API Grade X42 | 17.5 | 2415 | 2450 | 18988
2400150API Grade X42 | 2400 | 150 | API Grade X42 | 16.3333 | 2417.3333 | 2450 | 17865
2400160API Grade X42 | 2400 | 160 | API Grade X42 | 15.3125 | 2419.375 | 2450 | 16924
2400160API Grade X52 | 2400 | 160 | API Grade X52 | 15.3125 | 2419.375 | 2450 | 17190
2400160API Grade X65 | 2400 | 160 | API Grade X65 | 15.3125 | 2419.375 | 2450 | 17905
2500120API Grade X42 | 2500 | 120 | API Grade X42 | 21.1667 | 2497.6667 | 2540 | 23308
2500130API Grade X42 | 2500 | 130 | API Grade X42 | 19.5385 | 2500.9231 | 2540 | 21639
2500140API Grade X42 | 2500 | 140 | API Grade X42 | 18.1429 | 2503.7143 | 2540 | 20262
2500150API Grade X42 | 2500 | 150 | API Grade X42 | 16.9333 | 2506.1333 | 2540 | 19082
2500160API Grade X42 | 2500 | 160 | API Grade X42 | 15.875 | 2508.25 | 2540 | 18095
500100API Grade X42 | 500 | 100 | API Grade X42 | 5.08 | 497.84 | 508 | 1520.8374
500100API Grade X52 | 500 | 100 | API Grade X52 | 5.08 | 497.84 | 508 | 1552.7417
500100API Grade X65 | 500 | 100 | API Grade X65 | 5.08 | 497.84 | 508 | 1552.7417
500110API Grade X42 | 500 | 110 | API Grade X42 | 4.6182 | 498.7636 | 508 | 1420.2558
500110API Grade X52 | 500 | 110 | API Grade X52 | 4.6182 | 498.7636 | 508 | 1449.2863
500110API Grade X65 | 500 | 110 | API Grade X65 | 4.6182 | 498.7636 | 508 | 1449.2863
600100API Grade X42 | 600 | 100 | API Grade X42 | 6.1 | 597.8 | 610 | 2078.3634
600100API Grade X52 | 600 | 100 | API Grade X52 | 6.1 | 597.8 | 610 | 2124.366
600100API Grade X65 | 600 | 100 | API Grade X65 | 6.1 | 597.8 | 610 | 2124.366
600110API Grade X42 | 600 | 110 | API Grade X42 | 5.5455 | 598.9091 | 610 | 1933.3358
600110API Grade X52 | 600 | 110 | API Grade X52 | 5.5455 | 598.9091 | 610 | 1975.1947
600110API Grade X65 | 600 | 110 | API Grade X65 | 5.5455 | 598.9091 | 610 | 1975.1947
600120API Grade X42 | 600 | 120 | API Grade X42 | 5.0833 | 599.8333 | 610 | 1812.2741
600120API Grade X52 | 600 | 120 | API Grade X52 | 5.0833 | 599.8333 | 610 | 1850.6741
600120API Grade X65 | 600 | 120 | API Grade X65 | 5.0833 | 599.8333 | 610 | 1850.6741
600130API Grade X42 | 600 | 130 | API Grade X42 | 4.6923 | 600.6154 | 610 | 1709.6914
600130API Grade X52 | 600 | 130 | API Grade X52 | 4.6923 | 600.6154 | 610 | 1745.1605
600130API Grade X65 | 600 | 130 | API Grade X65 | 4.6923 | 600.6154 | 610 | 1745.1605
600140API Grade X42 | 600 | 140 | API Grade X42 | 4.3571 | 601.2857 | 610 | 1621.657
600140API Grade X52 | 600 | 140 | API Grade X52 | 4.3571 | 601.2857 | 610 | 1654.6108
600140API Grade X65 | 600 | 140 | API Grade X65 | 4.3571 | 601.2857 | 610 | 1654.6108
700100API Grade X42 | 700 | 100 | API Grade X42 | 7.11 | 696.78 | 711 | 2586
700100API Grade X52 | 700 | 100 | API Grade X52 | 7.11 | 696.78 | 711 | 2622
700100API Grade X65 | 700 | 100 | API Grade X65 | 7.11 | 696.78 | 711 | 2704
700110API Grade X42 | 700 | 110 | API Grade X42 | 6.4636 | 698.0727 | 711 | 2434
700110API Grade X52 | 700 | 110 | API Grade X52 | 6.4636 | 698.0727 | 711 | 2466
700110API Grade X65 | 700 | 110 | API Grade X65 | 6.4636 | 698.0727 | 711 | 2542
700120API Grade X42 | 700 | 120 | API Grade X42 | 5.925 | 699.15 | 711 | 2290
700120API Grade X52 | 700 | 120 | API Grade X52 | 5.925 | 699.15 | 711 | 2320
700120API Grade X65 | 700 | 120 | API Grade X65 | 5.925 | 699.15 | 711 | 2388
700130API Grade X42 | 700 | 130 | API Grade X42 | 5.4692 | 700.0615 | 711 | 2194
700130API Grade X52 | 700 | 130 | API Grade X52 | 5.4692 | 700.0615 | 711 | 2222
700130API Grade X65 | 700 | 130 | API Grade X65 | 5.4692 | 700.0615 | 711 | 2286
700140API Grade X42 | 700 | 140 | API Grade X42 | 5.0786 | 700.8429 | 711 | 2098
700140API Grade X52 | 700 | 140 | API Grade X52 | 5.0786 | 700.8429 | 711 | 2154
700140API Grade X65 | 700 | 140 | API Grade X65 | 5.0786 | 700.8429 | 711 | 2184
800100API Grade X42 | 800 | 100 | API Grade X42 | 8.13 | 796.74 | 813 | 3226
800100API Grade X52 | 800 | 100 | API Grade X52 | 8.13 | 796.74 | 813 | 3272
800100API Grade X65 | 800 | 100 | API Grade X65 | 8.13 | 796.74 | 813 | 3379
800110API Grade X42 | 800 | 110 | API Grade X42 | 7.3909 | 798.2182 | 813 | 3031
800110API Grade X52 | 800 | 110 | API Grade X52 | 7.3909 | 798.2182 | 813 | 3074
800110API Grade X65 | 800 | 110 | API Grade X65 | 7.3909 | 798.2182 | 813 | 3172
800120API Grade X42 | 800 | 120 | API Grade X42 | 6.775 | 799.45 | 813 | 2867
800120API Grade X52 | 800 | 120 | API Grade X52 | 6.775 | 799.45 | 813 | 2906
800120API Grade X65 | 800 | 120 | API Grade X65 | 6.775 | 799.45 | 813 | 2996
800130API Grade X42 | 800 | 130 | API Grade X42 | 6.2538 | 800.4923 | 813 | 2730
800130API Grade X52 | 800 | 130 | API Grade X52 | 6.2538 | 800.4923 | 813 | 2766
800130API Grade X65 | 800 | 130 | API Grade X65 | 6.2538 | 800.4923 | 813 | 2850
800140API Grade X42 | 800 | 140 | API Grade X42 | 5.8071 | 801.3857 | 813 | 2592
800140API Grade X52 | 800 | 140 | API Grade X52 | 5.8071 | 801.3857 | 813 | 2626
800140API Grade X65 | 800 | 140 | API Grade X65 | 5.8071 | 801.3857 | 813 | 2703
800150API Grade X42 | 800 | 150 | API Grade X42 | 5.42 | 802.16 | 813 | 2483
800150API Grade X52 | 800 | 150 | API Grade X52 | 5.42 | 802.16 | 813 | 2514
800150API Grade X65 | 800 | 150 | API Grade X65 | 5.42 | 802.16 | 813 | 2585
800160API Grade X42 | 800 | 160 | API Grade X42 | 5.0812 | 802.8375 | 813 | 2400
800160API Grade X52 | 800 | 160 | API Grade X52 | 5.0812 | 802.8375 | 813 | 2430
800160API Grade X65 | 800 | 160 | API Grade X65 | 5.0812 | 802.8375 | 813 | 2497
900100API Grade X42 | 900 | 100 | API Grade X42 | 9.14 | 895.72 | 914 | 3938
900100API Grade X52 | 900 | 100 | API Grade X52 | 9.14 | 895.72 | 914 | 3996
900100API Grade X65 | 900 | 100 | API Grade X65 | 9.14 | 895.72 | 914 | 4132
900110API Grade X42 | 900 | 110 | API Grade X42 | 8.3091 | 897.3818 | 914 | 3692
900110API Grade X52 | 900 | 110 | API Grade X52 | 8.3091 | 897.3818 | 914 | 3745
900110API Grade X65 | 900 | 110 | API Grade X65 | 8.3091 | 897.3818 | 914 | 3869
900120API Grade X42 | 900 | 120 | API Grade X42 | 7.6167 | 898.7667 | 914 | 3473
900120API Grade X52 | 900 | 120 | API Grade X52 | 7.6167 | 898.7667 | 914 | 3522
900120API Grade X65 | 900 | 120 | API Grade X65 | 7.6167 | 898.7667 | 914 | 3635
900130API Grade X42 | 900 | 130 | API Grade X42 | 7.0308 | 899.9385 | 914 | 3279
900130API Grade X52 | 900 | 130 | API Grade X52 | 7.0308 | 899.9385 | 914 | 3325
900130API Grade X65 | 900 | 130 | API Grade X65 | 7.0308 | 899.9385 | 914 | 3429
900140API Grade X42 | 900 | 140 | API Grade X42 | 6.5286 | 900.9429 | 914 | 3125
900140API Grade X52 | 900 | 140 | API Grade X52 | 6.5286 | 900.9429 | 914 | 3167
900140API Grade X65 | 900 | 140 | API Grade X65 | 6.5286 | 900.9429 | 914 | 3264
900150API Grade X42 | 900 | 150 | API Grade X42 | 6.0933 | 901.8133 | 914 | 3002
900150API Grade X52 | 900 | 150 | API Grade X52 | 6.0933 | 901.8133 | 914 | 3041
900150API Grade X65 | 900 | 150 | API Grade X65 | 6.0933 | 901.8133 | 914 | 3132
900160API Grade X42 | 900 | 160 | API Grade X42 | 5.7125 | 902.575 | 914 | 2878
900160API Grade X52 | 900 | 160 | API Grade X52 | 5.7125 | 902.575 | 914 | 2914
900160API Grade X65 | 900 | 160 | API Grade X65 | 5.7125 | 902.575 | 914 | 3000
328

## Crossings
River Crossing (below river bed level). Concrete encasement
| 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 2500 | 1
Ave Length | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 2 | m
Average Dia | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 2500 | 3 | mm
Side allowance | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 4 | mm
Vol CC/m | 1.2437 | 1.4073 | 1.5752 | 1.7473 | 1.9238 | 2.1046 | 2.2897 | 2.479 | 2.6727 | 2.8706 | 3.0729 | 3.2794 | 3.4902 | 3.7053 | 3.9247 | 4.1484 | 4.3764 | 4.6087 | 4.8452 | 5.0861 | 5.3313 | 5 | m^3/m
6
CC Volume | 62.1825 | 70.3628 | 78.7577 | 87.3673 | 96.1914 | 105.2301 | 114.4834 | 123.9513 | 133.6339 | 143.531 | 153.6427 | 163.969 | 174.51 | 185.2655 | 196.2356 | 207.4204 | 218.8197 | 230.4336 | 242.2622 | 254.3053 | 266.5631 | 7 | m^3
CC Rate | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 8 | R/m^3
Excavation | 191.7004 | 212.4172 | 234.4242 | 257.7538 | 281.9484 | 307.4873 | 334.1362 | 361.6177 | 390.476 | 420.1451 | 545.2876 | 580.6986 | 616.8561 | 654.4764 | 692.8216 | 773.9711 | 815.9308 | 859.0005 | 902.7418 | 952.9701 | 993.9497 | 9 | 69576.4802
Excvation Rate | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 10
11
Concrete | 111928.5413 | 126653.0995 | 141763.941 | 157261.0658 | 173144.4739 | 189414.1653 | 206070.14 | 223112.398 | 240540.9393 | 258355.764 | 276556.8719 | 295144.2632 | 314117.9377 | 333477.8956 | 353224.1367 | 373356.6612 | 393875.4689 | 414780.56 | 436071.9344 | 457749.5921 | 479813.5331 | 12
Excavation | 9585.0196 | 10620.8595 | 11721.2101 | 12887.6879 | 14097.4207 | 15374.3637 | 16706.8113 | 18080.8868 | 19523.7997 | 21007.2574 | 27264.3817 | 29034.928 | 30842.807 | 32723.8184 | 34641.0797 | 38698.5563 | 40796.5376 | 42950.0235 | 45137.088 | 47648.5064 | 49697.4859 | 13
Erosion Protection | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 14
EO for excavation/River diversion | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 15
Pipe materials (stainless steel) | 86791.6238 | 99882.708 | 130845 | 148850 | 178295 | 215670 | 251485 | 289250 | 333970 | 378495 | 429455 | 484575 | 539500 | 595790 | 664430 | 725335 | 797875 | 897195 | 967200 | 1054560 | 1130675 | 16
Total | 508305.1848 | 537156.6671 | 584330.1511 | 618998.7537 | 665536.8946 | 720458.529 | 774261.9513 | 830443.2849 | 894034.739 | 957858.0214 | 1033276.2537 | 1108754.1911 | 1184460.7447 | 1261991.714 | 1352295.2164 | 1437390.2175 | 1532547.0065 | 1654925.5836 | 1748409.0224 | 1859958.0985 | 1960186.0189 | 17
Rounded | 510000 | 540000 | 580000 | 620000 | 670000 | 720000 | 770000 | 830000 | 890000 | 960000 | 1030000 | 1110000 | 1180000 | 1260000 | 1350000 | 1440000 | 1530000 | 1650000 | 1750000 | 1860000 | 1960000 | 18
Gravel Road Crossing (Cut&cover concrete encased)
| 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 2500 | 1
Average length (m) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 2
Gravel wearing course | 13.59 | 14.49 | 15.399 | 16.317 | 17.226 | 18.144 | 19.062 | 19.971 | 20.889 | 21.798 | 22.716 | 23.634 | 24.543 | 25.461 | 26.37 | 29.088 | 30.006 | 30.924 | 31.833 | 32.85 | 33.66 | 3
WC Rate | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 4
CC Volume | 37.3095 | 42.2177 | 47.2546 | 52.4204 | 57.7148 | 63.1381 | 68.69 | 74.3708 | 80.1803 | 86.1186 | 92.1856 | 98.3814 | 104.706 | 111.1593 | 117.7414 | 124.4522 | 131.2918 | 138.2602 | 145.3573 | 152.5832 | 159.9378 | 5
CC Rate | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 6
Excavation | 115.0202 | 127.4503 | 140.6545 | 154.6523 | 169.169 | 184.4924 | 200.4817 | 216.9706 | 234.2856 | 252.0871 | 327.1726 | 348.4191 | 370.1137 | 392.6858 | 415.693 | 464.3827 | 489.5585 | 515.4003 | 541.6451 | 571.7821 | 596.3698 | 7
Excvation Rate | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 8
9
WC | 3397.5 | 3622.5 | 3849.75 | 4079.25 | 4306.5 | 4536 | 4765.5 | 4992.75 | 5222.25 | 5449.5 | 5679 | 5908.5 | 6135.75 | 6365.25 | 6592.5 | 7272 | 7501.5 | 7731 | 7958.25 | 8212.5 | 8415 | 10
Excavation | 5751.0118 | 6372.5157 | 7032.7261 | 7732.6127 | 8458.4524 | 9224.6182 | 10024.0868 | 10848.5321 | 11714.2798 | 12604.3544 | 16358.629 | 17420.9568 | 18505.6842 | 19634.2911 | 20784.6478 | 23219.1338 | 24477.9225 | 25770.0141 | 27082.2528 | 28589.1039 | 29818.4915 | 11
Concrete | 67157.1248 | 75991.8597 | 85058.3646 | 94356.6395 | 103886.6843 | 113648.4992 | 123642.084 | 133867.4388 | 144324.5636 | 155013.4584 | 165934.1231 | 177086.5579 | 188470.7626 | 200086.7373 | 211934.482 | 224013.9967 | 236325.2814 | 248868.336 | 261643.1606 | 274649.7553 | 287888.1199 | 12
Pipe materials (stainless steel) | 52074.9743 | 59929.6248 | 78507 | 89310 | 106977 | 129402 | 150891 | 173550 | 200382 | 227097 | 257673 | 290745 | 323700 | 357474 | 398658 | 435201 | 478725 | 538317 | 580320 | 632736 | 678405 | 13
Total | 128380.6109 | 145916.5002 | 174447.8407 | 195478.5022 | 223628.6368 | 256811.1174 | 289322.6708 | 323258.7209 | 361643.0934 | 400164.3128 | 445644.7522 | 491161.0147 | 536812.1968 | 583560.2784 | 637969.6298 | 689706.1305 | 747029.7039 | 820686.3501 | 877003.6635 | 944187.3591 | 1004526.6114 | 14
Rounded | 130000 | 150000 | 170000 | 200000 | 220000 | 260000 | 290000 | 320000 | 360000 | 400000 | 450000 | 490000 | 540000 | 580000 | 640000 | 690000 | 750000 | 820000 | 880000 | 940000 | 1000000 | 15
Road/Rail Crossing - steel pipe jacked
| 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 2500 | 1
Average length (m) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 2
Pipe jacking (R20 000 /m) | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 3
Pipe materials ( 2 x steel pipe cost) | 133525.5751 | 153665.7046 | 201300 | 229000 | 274300 | 331800 | 386900 | 445000 | 513800 | 582300 | 660700 | 745500 | 830000 | 916600 | 1022200 | 1115900 | 1227500 | 1380300 | 1488000 | 1622400 | 1739500 | 4
Total | 1133525.5751 | 1153665.7046 | 1201300 | 1229000 | 1274300 | 1331800 | 1386900 | 1445000 | 1513800 | 1582300 | 1660700 | 1745500 | 1830000 | 1916600 | 2022200 | 2115900 | 2227500 | 2380300 | 2488000 | 2622400 | 2739500 | 5
Rounded | 1130000 | 1150000 | 1200000 | 1230000 | 1270000 | 1330000 | 1390000 | 1450000 | 1510000 | 1580000 | 1660000 | 1750000 | 1830000 | 1920000 | 2020000 | 2120000 | 2230000 | 2380000 | 2490000 | 2620000 | 2740000 | 6
Provincial, National Road Crossing + Rail crossings (PJ)
1500 mm dia, 275m
Contract Value | 10500000
P&G's, H&S, Site establishment etc | 3000000
Construction Value | 7500000
Rate/m | 27272.7273
Esclated | 36068.1818
Pipe jacking rate (say) | 40000
Average length (prov road servitude = 48.8m) | 50
Cost/PJ | 2000000

## AV IV SV
Airvalve, scour & isolating budget estimate
Valve Chamber Cost Estimate
| Civil Rate/m | Mechanical Rate/m | Escalation Factor | Total
500 | 21 | 40 | 1.7 | 100
600 | 21 | 46 | 1.7 | 110
700 | 21 | 60 | 1.7 | 140
800 | 21 | 84 | 1.7 | 180
900 | 21 | 114.45 | 1.7 | 230
1000 | 23.1 | 144.9 | 1.7 | 290
1100 | 25.2 | 208.95 | 1.7 | 400
1200 | 27.3 | 273 | 1.7 | 510
1300 | 29.4 | 284.55 | 1.7 | 530
1400 | 29.4 | 296.1 | 1.7 | 550
1500 | 31.5 | 310.8 | 1.7 | 580
1600 | 33.6 | 329.7 | 1.7 | 620
1700 | 35.7 | 340.2 | 1.7 | 640
1800 | 37.8 | 352.8 | 1.7 | 660
1900 | 39.9 | 373.8 | 1.7 | 700
2000 | 42 | 401.1 | 1.7 | 750
2100 | 44.1 | 424.2 | 1.7 | 800
2200 | 46.2 | 447.3 | 1.7 | 840
2300 | 48.3 | 455.7 | 1.7 | 860
2400 | 50.4 | 478.8 | 1.7 | 900
2500 | 52.5 | 497.49 | 1.7 | 930

## Miscelanious
Electricity to Site | TBC
Detail Calc | 300000
Water to Site | TBC
Detail Calc | 300000
Accomodation | TBC
Detail Calc | 5000000
Cost of Relocations | TBC
Detail Calc | 10000000

## CP
Engineering |  | 156294
TRU |  | 489963
NDU |  | 141875
TP |  | 7281
FSX |  | 14281
MC |  | 6875
AC |  | 455244
AC |  | 150000
|  | TRU | NDU | TP | FSX | Coupon | AC Par | AFR Check | ICE | ICE Rounded | R/km | R/m
A | 8.88 | 1 | 0 | 19 | 0 | 3 | 5 | 5063037.72 | 5032102 | 5032000 | 566666.6667 | 566.6667
D | 7.025 | 1 | 0 | 15 | 0 | 3 | 1 | 2323012.35 | 2444644 | 2445000 | 348042.7046 | 348.0427
E | 7.17 | 1 | 0 | 15 | 3 | 3 | 1 | 2388517.98 | 2502336 | 2502000 | 348953.9749 | 348.954
F | 49.41 | 5 | 3 | 100 | 1 | 11 | 3 | 13231664.54 | 13873136 | 13873000 | 280773.1228 | 280.7731
[9 empty] | 23852218 | 23852000
386.1091
390

## Land Value
Sold Price | Code | Ha | R/Ha | R/Ha | Assume 50% of route is on mining land
30000 | M | 8.6 | 3502 | 3488.3721 | Average land value | 24000
3739600 | M | 203.7 | 18358 | 18358.3702 | Compensate 50% for right of use | 12000
3739600 | M | 200.3 | 18670 | 18669.995 | Compensate additional 25% for land claims | 18000
3739600 | M | 123.4 | 30308 | 30304.7002 | Compensate additional 25% for uncertianty/risk | 24000 | /ha
3739600 | M | 39.8 | 94052 | 93959.799
3739600 | M | 35.7 | 104835 | 104750.7003
Average |  |  |  | 40323.2161
25000 | P | 32.5 | 768 | 769.2308
182600 | P | 197.9 | 923 | 922.6882
280000 | P | 253.6 | 1104 | 1104.1009
550000 | P | 469.1 | 1172 | 1172.4579
195000 | P | 128.5 | 1518 | 1517.5097
700000 | P | 403 | 1737 | 1736.9727
225000 | P | 128.5 | 1751 | 1750.9728
250000 | P | 127.6 | 1959 | 1959.2476
1800000 | P | 915.1 | 1967 | 1966.9981
170000 | P | 85.7 | 1985 | 1983.6639
408716 | P | 192.9 | 2118 | 2118.7973
2300000 | P | 973 | 2364 | 2363.8232
750000 | P | 298.5 | 2513 | 2512.5628
220000 | P | 85.7 | 2568 | 2567.0945
680000 | P | 264.7 | 2569 | 2568.946
400000 | P | 152.2 | 2627 | 2628.1209
400000 | P | 152.2 | 2627 | 2628.1209
1400000 | P | 523 | 2677 | 2676.8642
2400000 | P | 850.8 | 2821 | 2820.8745
300000 | P | 105.6 | 2840 | 2840.9091
300000 | P | 105.6 | 2840 | 2840.9091
750000 | P | 224.3 | 3343 | 3343.7361
700000 | P | 194.4 | 3601 | 3600.823
800000 | P | 216.9 | 3688 | 3688.3356
800000 | P | 216.9 | 3688 | 3688.3356
352000 | P | 91.9 | 3832 | 3830.2503
525000 | P | 128.5 | 4086 | 4085.6031
2000000 | P | 486.7 | 4109 | 4109.3076
1000000 | P | 232.3 | 4305 | 4304.7783
600000 | P | 122.3 | 4907 | 4905.9689
930000 | P | 186 | 5001 | 5000
930000 | P | 186 | 5001 | 5000
2500000 | P | 495.8 | 5042 | 5042.3558
280000 | P | 51.9 | 5400 | 5394.9904
600000 | P | 111.1 | 5399 | 5400.5401
1000000 | P | 180.9 | 5528 | 5527.916
1500000 | P | 257 | 5837 | 5836.5759
1500000 | P | 234.9 | 6385 | 6385.696
2000000 | P | 299.8 | 6671 | 6671.1141
1000000 | P | 145.3 | 6884 | 6882.3125
1000000 | P | 145.3 | 6884 | 6882.3125
1000000 | P | 141.8 | 7052 | 7052.1862
1000000 | P | 141.8 | 7052 | 7052.1862
680000 | P | 95.8 | 7102 | 7098.1211
2500000 | P | 342.6 | 7297 | 7297.1395
1000000 | P | 132.4 | 7551 | 7552.8701
1000000 | P | 132.4 | 7551 | 7552.8701
2000000 | P | 259.9 | 7696 | 7695.2674
2000000 | P | 259.9 | 7696 | 7695.2674
1000000 | P | 123.6 | 8088 | 8090.6149
795000 | P | 96.8 | 8216 | 8212.8099
550000 | P | 44.8 | 12273 | 12276.7857
470000 | P | 34.2 | 13725 | 13742.6901
600000 | P | 42.8 | 14010 | 14018.6916
795000 | P | 50.4 | 15780 | 15773.8095
795000 | P | 50.4 | 15779 | 15773.8095
600000 | P | 21.8 | 27463 | 27522.9358
250000 | P | 8.1 | 30700 | 30864.1975
1500000 | P | 36.4 | 41154 | 41208.7912
250000 | P | 4.4 | 56276 | 56818.1818
280000 | P | 1.8 | 155538 | 155555.5556
1500000 | P | 8.6 | 174601 | 174418.6047
600000 | P | 1.7 | 350242 | 352941.1765
Average |  |  |  | 7781.3162
Souce: SPI Transfer records

## Roads
Budget costs for access roads - W Davel - 26/04/2007
Cost per m^2 | 800 | Normal
Cost / km | 6000000 | Normal
EO for bridge | 2000000 | Low level culverts
Gravel access along pipe | 10000