ANNEXURE 2

WEST COAST LANGEBAAN AQUIFER

An injection test was done but only 40 days of use could be recharged before the aquifer overflowed.  The current groundwater is abstracted from a bottom confined aquifer and water was injected in to this confined aquifer.  Unfortunately, numerous boreholes have been drilled into this confined aquifer – many of which did not seal off the upper unconfined aquifer with this bottom confined aquifer; and thus created a connection path between the two aquifers.  Therefore, any water pumped into the confined aquifer just flows out into the upper unconfined aquifer.

Artificial injection at the abstraction borehole has been put on hold, and other methods to increase the recharge to the well-field are being investigated.  This will entail increasing the recharge with infiltration canals or basins.  These canals or basins must be upstream of the well-field (1 – 3 km away), or at the recharge area of the well-field (10 -15 km away).

By the next meeting recommendations will be available on possible options to investigate further.