## Slide 1: Continuation of the Integrated Vaal River System Reconciliation Strategy Study (Phase 2)
Status report on water losses
Dry-run meeting - 20 February 2018
Willem Wegelin

## Slide 2: Background
Baseline study completed in 2004/2005
An estimated 196 million m3 or 15% could be saved over a period of 10 years
Average consumption was expected to reduce from 330 ℓ/c/d to 290 ℓ/c/d
The four biggest municipalities were expected to contribute 94.3% of the total saving
The targets set in 2005 were revised in 2010 and 2012

## Slide 3: Expected savings per municipality
Area | 2008/09 Annual Demand (million m³/a) | Current Non-Revenue Water (million m³/a) | 2005/06 Possible Savings (million m³/a) | % Contribution of total saving | % Reduction
City of Johannesburg | 502.7 | 160.9 | 110.2 | 56.2% | 21.9%
Ekurhuleni | 326.8 | 124.2 | 28.3 | 14.4% | 8.6%
City of Tshwane | 214.2 | 62.1 | 20.4 | 10.4% | 9.5%
Emfuleni | 77.1 | 31.6 | 26.1 | 13.3% | 33.9%
Rustenburg | 27.9 | 9.8 | 3.0 | 1.5% | 10.6%
Mogale | 26.4 | 7.1 | 1.7 | 0.9% | 6.6%
Govan Mbeki | 20.4 | 5.9 | 1.5 | 0.8% | 7.5%
Matjhabeng | 18.9 | 6.6 | 4.3 | 2.2% | 22.9%
Randfontein | 8.7 | 2.6 | 0.4 | 0.2% | 4.1%
Total | 1 223.0 | 410.8 | 195.9 | 100% | 16%

## Slide 4: Summary of data submissions
Municipality | Last submission
City of Johannesburg | November 2016
City of Tshwane | April 2017
Emfuleni LM | June 2017
Ekurhuleni MM | November 2017
Lesedi LM | April 2017
Merafong LM | June 2017
Midvaal LM | October 2017
Mogale City LM | December 2016
Rand West City LM (Randfontein Region) | June 2017
Rand West City LM (Westonaria Region) | November 2017

## Slide 5: Integrated Vaal River System
Chart: System Input Volume (m³/annum)
| 39600 | 39965 | 40330 | 40695 | 41061 | 41426 | 41791 | 42156 | 42339 | 42522 | 42705 | 42887 | 44713
Billed metered | 724355243 | 734622018.5 | 712310669.44 | 751569887 | 800726234 | 829480030.7278 | 816014162.6775 | 789296260.5 | 798432417.9809 | 793125390.5938 | 772842408 | 782956475 | 930400000
Billed unmetered | 44584883.925 | 39402048 | 45590595 | 40457651 | 42893326 | 47241260 | 50269683 | 106615067 | 109297086 | 115483320 | 114189870 | 101668394 | 105500000
Non-Revenue water | 396094465.075 | 430596412.3475 | 425043280.56 | 491349160 | 452453655 | 460814954.2722 | 499096333.7409 | 507611798.5 | 512372385.0191 | 504422576.4062 | 489094781 | 400650960 | 337214426
Projected SIV without WDM | 1300613343 | 1325208539 | 1350262570 | 1375784167 | 1388841059.75 | 1401897952.5 | 1414954845.25 | 1425052022 | 1554334603
Projected SIV with WDM | 1300613343 | 1273402875 | 1268011188 | 1262935804 | 1261797858.75 | 1260659913.5 | 1259521968.25 | 1260965718.75 | 1373114426
% Non-revenue water | 0.33999 | 0.35745 | 0.35931 | 0.38286 | 0.3491 | 0.34453 | 0.36554 | 0.36167 | 0.3608 | 0.35698 | 0.35541 | 0.31172 | 0.24558
15% Water restrictions 12 Aug 2016 to 13 March 2017
Target
Target

## Slide 6: Total targeted vs actual savings
Year ending | Projected SIV without WDM (X) kl/annum | Projected SIV with WDM (Z) kl/annum | Projected % savings (X – Z) / X * 100 | Actual demand (Y) kl/annum | Actual % savings (X - Y) / X * 100
Jun-12 | 1 300 613 343 | 1 300 613 343 | 0.0% | 1 296 073 215 | 0.3%
Jun-13 | 1 325 208 539 | 1 273 402 875 | 3.9% | 1 337 536 245 | -0.9%
Jun-14 | 1 350 262 570 | 1 268 011 188 | 6.1% | 1 365 380 179 | -1.1%
Jun-15 | 1 375 784 167 | 1 262 935 804 | 8.2% | 1 403 523 126 | -2.0%
Dec-15 | 1 388 841 060 | 1 261 797 859 | 9.1% | 1 420 101 889 | -2.3%
Jun-16 | 1 401 897 953 | 1 260 659 914 | 10.1% | 1 413 031 287 | -0.8%
Dec-16 | 1 414 954 845 | 1 259 521 968 | 11.0% | 1 374 064 291 | 2.9%
Jun-17 | 1 424 217 581 | 1 261 854 997 | 11.4% |  | 
Jun-22 | 1 554 334 603 | 1 373 114 426 | 11.7% |  | 

## Slide 7: Dec 2016 summary of targeted vs actual savings
System | Projected SIV without WDM (X) kl/annum | Projected SIV with WDM (Z) kl/annum | Projected % savings (X – Z) / X * 100 | Actual demand (Y) kl/annum | Actual % savings (X - Y) / X * 100
Johannesburg | 588 066 982 | 493 829 325 | 16.0% | 573 852 765 | 2.4%
Tshwane | 341 884 714 | 327 517 148 | 4.2% | 332 387 892 | 2.8%
Ekurhuleni | 369 315 955 | 346 720 055 | 6.1% | 352 297 242 | 4.6%
Emfuleni | 93 946 677 | 70 942 157 | 24.5% | 95 965 374 | -2.1%
Midvaal | 14 756 008 | 13 853 121 | 6.1% | 12 639 915 | 14.3%
Lesedi | 6 984 510 | 6 660 163 | 4.6% | 6 921 103 | 0.9%
Mogale City* | 29 553 459 | 27 943 452 | 5.4% | 33 408 509 | -13.0%
Randfontein* | 9 903 720 | 9 589 349 | 3.2% | 9 668 710 | 2.4%
Westonaria* | 7 192 187 | 6 460 157 | 10.2% | 0 | 
Merafong City* | 13 324 128 | 12 056 011 | 9.5% | 13 476 658 | -1.1%
Total | 1 474 928 340 | 1 315 570 936 | 10.8% | 1 430 618 168 | 3.0%
*Total excl West Rand DM | 1 414 954 845 | 1 259 521 968 | 11.0% | 1 374 064 291 | 2.9%

## Slide 8: 2016 IVRS Water balance
Chart: 
 | 1374.0643 | 389.3784 | 277.7566 | 277.7566 | 480.4867
 | 984.6859 | 111.6218 | 111.6218 | 893.5776
 | 91.1083 | 90.569
 | 893.5776 | 0.53935
 | 114.9598
 | 778.6178
65.0%
35.0%
28.3%

## Slide 9: IVRS litres/capita/day
Chart: Population
| 39600 | 39965 | 40330 | 40695 | 41061 | 41426 | 41791 | 42156 | 42339 | 42522 | 42705 | 42887 | 44713
Population served | 10070614 | 10160734 | 11184241 | 11292001 | 11379351 | 11467477.9937 | 12320990 | 12486676.9312 | 12486676.9312 | 12558497 | 12558497 | 12498117.679 | 13360348.5292
blank
blank
Litres / capita / day | 316.9495 | 324.8122 | 289.7777 | 307.5476 | 307.8127 | 314.2489 | 298.6034 | 303.0514 | 306.9026 | 302.2593 | 296.1631 | 277.1371 | 277.0444

## Slide 10: Conclusions
Updated water balance information required to assess the status quo.
It is expected that the demand returned to previous levels once the water restrictions were lifted
It is unlikely that municipalities in the IVRS have been able to reduce their consumption by 112 million m3/a or 9% to achieve the 2017 target
Most municipalities are tracking the High demand – no WCWDM scenario

## Slide 11: Thank you